## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 11 | 12 | 8 | 14 | 3.4 | 22.51 | 50 | 104.5 | 18.8 | 17.4 | 36.9 | 226.1 | 198.1 | 198.1 | NO
| NG | 12 | 14 | 8 | 14 | 3.4 | 17.84 | 50 | 104.5 | 18.8 | 35.5 | 32.6 | 221.6 | 208 | 208 | NO
| NG | 14 | 13 | 8 | 14 | 3.4 | 16.47 | 50 | 104.5 | 18.8 | 40.7 | 31.5 | 220.5 | 209.8 | 209.8 | NO
1 | ** OPTIMAL ** | 13 | 9 | 8 | 14 | 3.4 | 7.85 | 50 | 104.5 | 18.8 | 73.8 | 24.6 | 213.4 | 220.6 | 213.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-007443
TR_B (available) | 59-019094
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 104.5
TR_B Baseline Loading% | 18.8
Total Scenarios Evaluated | 4
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 9
Tie Node (TR_A side) | 8
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 3.4
Load Transferred (kW) | 7.85
TR_A Loading After (%) | 73.8
TR_B Loading After (%) | 24.6
Minimum Voltage (V) | 213.4