## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 21 | 22 | 31 | 41 | 3.5 | 18.77 | 50 | 83.3 | 6.9 | 8.6 | 8.2 | 229.4 | 222.2 | 222.2 | YES
2 | OK | 21 | 54 | 65 | 41 | 8.2 | 13.26 | 50 | 83.3 | 6.9 | 52.3 | 6.9 | 218.8 | 222.5 | 218.8 | YES
3 | ** OPTIMAL ** | 22 | 32 | 31 | 41 | 3.5 | 15.2 | 50 | 83.3 | 6.9 | 23.1 | 8.2 | 226.9 | 222.2 | 222.2 | YES
4 | OK | 54 | 50 | 65 | 41 | 8.2 | 10.16 | 50 | 83.3 | 6.9 | 59.5 | 6.9 | 218.3 | 222.5 | 218.3 | YES
5 | OK | 32 | 33 | 31 | 41 | 3.5 | 15.2 | 50 | 83.3 | 6.9 | 27.5 | 8.2 | 226.2 | 222.2 | 222.2 | YES
6 | OK | 50 | 51 | 65 | 41 | 8.2 | 8.62 | 50 | 83.3 | 6.9 | 63 | 6.9 | 218.3 | 222.5 | 218.3 | YES
7 | OK | 33 | 34 | 31 | 41 | 3.5 | 15.2 | 50 | 83.3 | 6.9 | 31.6 | 8.2 | 225.8 | 222.2 | 222.2 | YES
8 | OK | 51 | 68 | 65 | 41 | 8.2 | 6.8 | 50 | 83.3 | 6.9 | 67.2 | 6.9 | 217.7 | 222.5 | 217.7 | YES
9 | OK | 34 | 35 | 31 | 41 | 3.5 | 7.8 | 50 | 83.3 | 6.9 | 48.9 | 8.2 | 220.4 | 222.2 | 220.4 | YES
10 | OK | 68 | 59 | 65 | 41 | 8.2 | 5.84 | 50 | 83.3 | 6.9 | 69.5 | 6.9 | 217 | 222.5 | 217 | YES
11 | OK | 35 | 36 | 31 | 41 | 3.5 | 6.91 | 50 | 83.3 | 6.9 | 53.2 | 7.6 | 219.8 | 222.3 | 219.8 | YES
12 | OK | 59 | 60 | 65 | 41 | 8.2 | 4.58 | 50 | 83.3 | 6.9 | 72.4 | 6.9 | 216.9 | 222.5 | 216.9 | YES
13 | OK | 36 | 37 | 31 | 41 | 3.5 | 6.91 | 50 | 83.3 | 6.9 | 56.1 | 7.6 | 219.7 | 222.3 | 219.7 | YES
14 | OK | 37 | 38 | 31 | 41 | 3.5 | 6.64 | 50 | 83.3 | 6.9 | 56.7 | 7.5 | 219.7 | 222.4 | 219.7 | YES
15 | OK | 38 | 39 | 31 | 41 | 3.5 | 6.31 | 50 | 83.3 | 6.9 | 56.8 | 7.5 | 219.7 | 222.4 | 219.7 | YES
16 | OK | 39 | 40 | 31 | 41 | 3.5 | 5.2 | 50 | 83.3 | 6.9 | 60.1 | 7.2 | 218.9 | 222.4 | 218.9 | YES
17 | OK | 40 | 41 | 31 | 41 | 3.5 | 5.1 | 50 | 83.3 | 6.9 | 67.6 | 7.2 | 216.7 | 222.4 | 216.7 | YES
18 | OK | 41 | 42 | 31 | 41 | 3.5 | 4.35 | 50 | 83.3 | 6.9 | 73 | 7.2 | 215.3 | 222.4 | 215.3 | YES
19 | OK | 42 | 43 | 31 | 41 | 3.5 | 3.63 | 50 | 83.3 | 6.9 | 74.7 | 6.9 | 214.8 | 222.5 | 214.8 | YES
20 | OK | 43 | 69 | 31 | 41 | 3.5 | 2.89 | 50 | 83.3 | 6.9 | 76.5 | 6.9 | 213 | 222.5 | 213 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 57-008159
TR_B (available) | 40-023596
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 83.3
TR_B Baseline Loading% | 6.9
Total Scenarios Evaluated | 20
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 32
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 41
Tie Line Distance (m) | 3.5
Load Transferred (kW) | 15.2
TR_A Loading After (%) | 23.1
TR_B Loading After (%) | 8.2
Minimum Voltage (V) | 222.2