## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 53 | 5 | 30 | 113 | 21.5 | 2.45 | 50 | 45.4 | 20.9 | 42.5 | 21.8 | 211.1 | 216.3 | 211.1 | YES
| NG | 5 | 4 | 30 | 113 | 21.5 | 2.45 | 50 | 45.4 | 20.9 | 42.5 | 21.8 | 47.8 | 216.3 | 47.8 | NO
| NG | 4 | 14 | 14 | 46 | 87.4 | 1.77 | 50 | 45.4 | 20.9 | 45.1 | 21 | 47.5 | 216.4 | 47.5 | NO
2 | OK | 4 | 28 | 30 | 113 | 21.5 | 0.68 | 50 | 45.4 | 20.9 | 42.8 | 21.7 | 211 | 216.3 | 211 | YES
3 | OK | 14 | 15 | 15 | 46 | 126.7 | 1.57 | 50 | 45.4 | 20.9 | 45.1 | 21 | 210.5 | 216.4 | 210.5 | YES
4 | OK | 28 | 27 | 27 | 12 | 86.4 | 0.48 | 50 | 45.4 | 20.9 | 43.5 | 21.5 | 210.9 | 216.3 | 210.9 | YES
5 | OK | 28 | 29 | 30 | 113 | 21.5 | 0.2 | 50 | 45.4 | 20.9 | 44.6 | 21.1 | 210.6 | 216.4 | 210.6 | YES
| NG | 29 | 30 | 30 | 113 | 21.5 | 0.2 | 50 | 45.4 | 20.9 | 44.6 | 7434.4 | 210.6 | 37.2 | 37.2 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 57-009162
TR_B (available) | 29-013821
TR_A Rated kVA | 30
TR_B Rated kVA | 100
TR_A Baseline Loading% | 45.4
TR_B Baseline Loading% | 20.9
Total Scenarios Evaluated | 8
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 53
Switch Child Node | 5
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 113
Tie Line Distance (m) | 21.5
Load Transferred (kW) | 2.45
TR_A Loading After (%) | 42.5
TR_B Loading After (%) | 21.8
Minimum Voltage (V) | 211.1