## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 54 | 53 | 52 | 18 | 1.6 | 11.59 | 50 | 74.8 | 2.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 54 | 58 | 58 | 27 | 3.1 | 18.14 | 50 | 74.8 | 2.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 53 | 18 | 52 | 18 | 1.6 | 11.59 | 50 | 74.8 | 2.2 | 46.9 | 53.9 | 184.8 | 184.9 | 184.8 | NO
| NG | 58 | 15 | 15 | 27 | 18.6 | 17.87 | 50 | 74.8 | 2.2 | 28 | 102.2 | 215.7 | 134.5 | 134.5 | NO
| NG | 18 | 7 | 52 | 18 | 1.6 | 11.59 | 50 | 74.8 | 2.2 | 46.9 | 53.9 | 184.8 | 184.9 | 184.8 | NO
| NG | 15 | 16 | 16 | 27 | 19.5 | 2.35 | 50 | 74.8 | 2.2 | 69.2 | 2.2 | 179 | 230.5 | 179 | NO
| NG | 15 | 55 | 55 | 26 | 19 | 15.46 | 50 | 74.8 | 2.2 | 33.5 | 73.7 | 214.5 | 173.7 | 173.7 | NO
| NG | 7 | 8 | 8 | 1 | 48.4 | 2.23 | 50 | 74.8 | 2.2 | 68.5 | 10.9 | 178.8 | 223.8 | 178.8 | NO
| NG | 7 | 66 | 52 | 18 | 1.6 | 9.36 | 50 | 74.8 | 2.2 | 52.1 | 39.1 | 183.4 | 197.6 | 183.4 | NO
| NG | 55 | 24 | 25 | 4 | 27.4 | 12.43 | 50 | 74.8 | 2.2 | 40.6 | 53.6 | 213 | 201.7 | 201.7 | NO
| NG | 55 | 59 | 59 | 26 | 19.3 | 3.03 | 50 | 74.8 | 2.2 | 67 | 14 | 181.4 | 223.8 | 181.4 | NO
| NG | 8 | 12 | 0 | 14 | 52 | 2.23 | 50 | 74.8 | 2.2 | 68.5 | 10.9 | 178.8 | 223.8 | 178.8 | NO
| NG | 66 | 52 | 52 | 18 | 1.6 | 9.24 | 50 | 74.8 | 2.2 | 52.4 | 39.1 | 183.4 | 197.6 | 183.4 | NO
| NG | 24 | 30 | 30 | 4 | 69.5 | 12.43 | 50 | 74.8 | 2.2 | 40.6 | 53.2 | 213 | 203.5 | 203.5 | NO
| NG | 59 | 61 | 61 | 26 | 45.1 | 3.03 | 50 | 74.8 | 2.2 | 67 | 14 | 181.4 | 223.9 | 181.4 | NO
| NG | 12 | 50 | 0 | 14 | 52 | 2.23 | 50 | 74.8 | 2.2 | 68.5 | 10.9 | 178.8 | 223.8 | 178.8 | NO
| NG | 52 | 35 | 21 | 17 | 3.2 | 8.66 | 50 | 74.8 | 2.2 | 52.4 | 39.3 | 183.4 | 183 | 183 | NO
| NG | 30 | 32 | 32 | 4 | 84.4 | 11.35 | 50 | 74.8 | 2.2 | 43.1 | 48.6 | 212.4 | 205.6 | 205.6 | NO
| NG | 61 | 62 | 62 | 25 | 60 | 2.07 | 50 | 74.8 | 2.2 | 69.5 | 10.2 | 180 | 226.6 | 180 | NO
| NG | 50 | 10 | 0 | 14 | 52 | 2.23 | 50 | 74.8 | 2.2 | 68.5 | 10.9 | 178.8 | 223.8 | 178.8 | NO
| NG | 35 | 14 | 49 | 18 | 18.8 | 7.84 | 50 | 74.8 | 2.2 | 55.7 | 32.6 | 182.5 | 202.5 | 182.5 | NO
| NG | 35 | 19 | 21 | 17 | 3.2 | 0.82 | 50 | 74.8 | 2.2 | 72.8 | 5.4 | 177.6 | 227.1 | 177.6 | NO
1 | OK | 32 | 63 | 65 | 24 | 112.1 | 10.11 | 50 | 74.8 | 2.2 | 46.1 | 42.8 | 211.7 | 210.6 | 210.6 | YES
| NG | 10 | 11 | 0 | 14 | 52 | 2.23 | 50 | 74.8 | 2.2 | 68.5 | 10.9 | 178.8 | 223.8 | 178.8 | NO
| NG | 14 | 4 | 43 | 14 | 50 | 7.84 | 50 | 74.8 | 2.2 | 55.7 | 32.5 | 182.5 | 202.7 | 182.5 | NO
| NG | 19 | 20 | 20 | 16 | 39.7 | 0.82 | 50 | 74.8 | 2.2 | 72.8 | 5.4 | 177.6 | 227.7 | 177.6 | NO
2 | OK | 63 | 64 | 65 | 24 | 112.1 | 10.11 | 50 | 74.8 | 2.2 | 46.1 | 42.8 | 211.7 | 210.6 | 210.6 | YES
| NG | 11 | 13 | 0 | 14 | 52 | 0.76 | 50 | 74.8 | 2.2 | 73.5 | 5.2 | 177.4 | 228.3 | 177.4 | NO
| NG | 4 | 9 | 9 | 20 | 53 | 0.25 | 50 | 74.8 | 2.2 | 74.2 | 3.2 | 177.2 | 229.8 | 177.2 | NO
| NG | 4 | 3 | 43 | 14 | 50 | 1.34 | 50 | 74.8 | 2.2 | 71.9 | 5 | 177.8 | 228.3 | 177.8 | NO
| NG | 4 | 6 | 38 | 14 | 81.5 | 4.39 | 50 | 74.8 | 2.2 | 63.9 | 20 | 180.1 | 213.7 | 180.1 | NO
3 | ** OPTIMAL ** | 64 | 28 | 28 | 24 | 157.6 | 10.11 | 50 | 74.8 | 2.2 | 46.1 | 42.7 | 211.7 | 211.5 | 211.5 | YES
| NG | 13 | 0 | 0 | 14 | 52 | 0.76 | 50 | 74.8 | 2.2 | 73.5 | 5.2 | 177.4 | 228.3 | 177.4 | NO
| NG | 3 | 2 | 2 | 20 | 58.9 | 0.71 | 50 | 74.8 | 2.2 | 73.4 | 5 | 177.4 | 228.3 | 177.4 | NO
| NG | 3 | 45 | 43 | 14 | 50 | 0.63 | 50 | 74.8 | 2.2 | 73.3 | 2.2 | 177.4 | 230.5 | 177.4 | NO
| NG | 6 | 5 | 38 | 14 | 81.5 | 0.71 | 50 | 74.8 | 2.2 | 73.1 | 5 | 177.5 | 228.3 | 177.5 | NO
| NG | 6 | 22 | 22 | 18 | 93.6 | 3.68 | 50 | 74.8 | 2.2 | 65.6 | 17 | 179.6 | 216 | 179.6 | NO
| NG | 28 | 29 | 34 | 10 | 157.7 | 6.92 | 50 | 74.8 | 2.2 | 54.1 | 29.2 | 205.8 | 219.6 | 205.8 | NO
| NG | 0 | 1 | 1 | 14 | 52.5 | 0.76 | 50 | 74.8 | 2.2 | 73.5 | 2.2 | 177.4 | 230.5 | 177.4 | NO
| NG | 45 | 43 | 43 | 14 | 50 | 0.63 | 50 | 74.8 | 2.2 | 73.3 | 2.2 | 177.4 | 230.5 | 177.4 | NO
| NG | 5 | 38 | 38 | 14 | 81.5 | 0.51 | 50 | 74.8 | 2.2 | 73.6 | 4.2 | 177.3 | 228.9 | 177.3 | NO
| NG | 22 | 39 | 39 | 18 | 95.9 | 3.68 | 50 | 74.8 | 2.2 | 65.6 | 17 | 179.6 | 216 | 179.6 | NO
| NG | 29 | 33 | 34 | 10 | 157.7 | 5.88 | 50 | 74.8 | 2.2 | 56.9 | 25.1 | 202.4 | 221.2 | 202.4 | NO
| NG | 43 | 44 | 44 | 14 | 53.5 | 0.63 | 50 | 74.8 | 2.2 | 73.3 | 2.2 | 177.4 | 230.5 | 177.4 | NO
| NG | 38 | 41 | 41 | 14 | 107.4 | 0.51 | 50 | 74.8 | 2.2 | 73.6 | 4.2 | 177.3 | 228.9 | 177.3 | NO
| NG | 39 | 40 | 40 | 16 | 192.1 | 3.68 | 50 | 74.8 | 2.2 | 65.6 | 17.1 | 179.6 | 215.1 | 179.6 | NO
| NG | 33 | 34 | 34 | 10 | 157.7 | 3.01 | 50 | 74.8 | 2.2 | 65.1 | 13.8 | 190 | 226.4 | 190 | NO
| NG | 33 | 60 | 57 | 6 | 173.5 | 2.87 | 50 | 74.8 | 2.2 | 65.5 | 13.4 | 190.7 | 224.4 | 190.7 | NO
| NG | 41 | 37 | 37 | 14 | 131 | 0.39 | 50 | 74.8 | 2.2 | 73.9 | 3.7 | 177.3 | 229.3 | 177.3 | NO
| NG | 60 | 56 | 57 | 6 | 173.5 | 2.25 | 50 | 74.8 | 2.2 | 67.4 | 10.9 | 188.2 | 225.8 | 188.2 | NO
| NG | 56 | 26 | 57 | 6 | 173.5 | 2.25 | 50 | 74.8 | 2.2 | 67.4 | 5 | 188.2 | 229.4 | 188.2 | NO
| NG | 26 | 27 | 57 | 6 | 173.5 | 0.71 | 50 | 74.8 | 2.2 | 72.4 | 5 | 181.1 | 229.4 | 181.1 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 57-940127
TR_B (available) | 64-008687
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 74.8
TR_B Baseline Loading% | 2.2
Total Scenarios Evaluated | 52
Feasible Scenarios | 3
--- Optimal Solution ---
Switch Parent Node | 64
Switch Child Node | 28
Tie Node (TR_A side) | 28
Tie Node (TR_B side) | 24
Tie Line Distance (m) | 157.6
Load Transferred (kW) | 10.11
TR_A Loading After (%) | 46.1
TR_B Loading After (%) | 42.7
Minimum Voltage (V) | 211.5