## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 62 | 57 | 57 | 2 | 149 | 1.69 | 50 | 76.2 | 8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 61 | 29 | 42 | 2 | 6.5 | 19.27 | 50 | 76.2 | 8 | 19 | 32.2 | 223.1 | 215.2 | 215.2 | YES
| NG | 61 | 30 | 30 | 2 | 113.7 | 6.41 | 50 | 76.2 | 8 | 0 | 16.4 | 0 | 224.5 | 0 | NO
| NG | 61 | 63 | 65 | 2 | 43.5 | 0.39 | 50 | 76.2 | 8 | 74.6 | 8 | 190.4 | 227.4 | 190.4 | NO
| NG | 57 | 58 | 58 | 2 | 190.8 | 1 | 50 | 76.2 | 8 | 76.2 |  | 190 | 9.3752e+77 | 190 | NO
2 | OK | 29 | 27 | 42 | 2 | 6.5 | 18.62 | 50 | 76.2 | 8 | 22.3 | 32.2 | 222.5 | 215.2 | 215.2 | YES
| NG | 30 | 26 | 26 | 2 | 151.8 | 5.69 | 50 | 76.2 | 8 | 0 | 15.9 | 30 | 224.8 | 30 | NO
| NG | 63 | 64 | 65 | 2 | 43.5 | 0.39 | 50 | 76.2 | 8 | 74.6 | 8 | 190.4 | 227.4 | 190.4 | NO
3 | OK | 27 | 28 | 42 | 2 | 6.5 | 17.4 | 50 | 76.2 | 8 | 23.4 | 28.4 | 222.3 | 216.8 | 216.8 | YES
| NG | 26 | 14 | 14 | 2 | 184.5 | 5.13 | 50 | 76.2 | 8 | [5 empty] | NO | TR_A sim: not converged
| NG | 64 | 65 | 65 | 2 | 43.5 | 0.17 | 50 | 76.2 | 8 | 75.5 | 8 | 190.2 | 227.4 | 190.2 | NO
4 | OK | 28 | 41 | 42 | 2 | 6.5 | 16.57 | 50 | 76.2 | 8 | 27.2 | 28.4 | 221.5 | 216.8 | 216.8 | YES
| NG | 14 | 13 | 13 | 2 | 193.3 | 0.29 | 50 | 76.2 | 8 | 76.2 | 9.1 | 190 | 227.2 | 190 | NO
| NG | 14 | 31 | 31 | 2 | 192.9 | 4.64 | 50 | 76.2 | 8 |  | 11.8 | 5.0808e+58 | 226.7 | 226.7 | NO
| NG | 41 | 42 | 42 | 2 | 6.5 | 2.73 | 50 | 76.2 | 8 | 76.2 | 18.6 | 190 | 223.9 | 190 | NO
5 | OK | 41 | 56 | 56 | 2 | 45.7 | 13.84 | 50 | 76.2 | 8 | 27.2 | 17.6 | 221.5 | 221.3 | 221.3 | YES
| NG | 13 | 12 | 12 | 2 | 216.3 | 0.26 | 50 | 76.2 | 8 | 76.2 | 9 | 190 | 227.2 | 190 | NO
| NG | 42 | 50 | 50 | 2 | 50.2 | 2.73 | 50 | 76.2 | 8 | 76.2 | 18.6 | 190 | 224 | 190 | NO
6 | OK | 56 | 37 | 37 | 2 | 48.5 | 13.84 | 50 | 76.2 | 8 | 27.2 | 17.6 | 221.5 | 221.3 | 221.3 | YES
| NG | 50 | 49 | 49 | 2 | 88.2 | 1.79 | 50 | 76.2 | 8 | 76.2 | 14.9 | 190 | 225.6 | 190 | NO
7 | OK | 37 | 38 | 38 | 2 | 90.8 | 13.84 | 50 | 76.2 | 8 | 27.2 | 17.6 | 221.5 | 221.3 | 221.3 | YES
| NG | 49 | 22 | 22 | 2 | 125.4 | 1.54 | 50 | 76.2 | 8 | 76.2 | 14 | 190 | 226 | 190 | NO
8 | OK | 38 | 40 | 10 | 2 | 121.9 | 13.77 | 50 | 76.2 | 8 | 27.5 | 17.6 | 221.5 | 221.1 | 221.1 | YES
| NG | 22 | 23 | 23 | 2 | 169 | 1.43 | 50 | 76.2 | 8 | 76.2 | 13.5 | 190 | 226.2 | 190 | NO
9 | ** OPTIMAL ** | 40 | 10 | 10 | 2 | 121.9 | 11.57 | 50 | 76.2 | 8 | 27.5 | 9 | 221.5 | 227.2 | 221.5 | YES
| NG | 40 | 36 | 36 | 2 | 130.8 | 2.2 | 50 | 76.2 | 8 | 76.2 | 16.6 | 190 | 221.8 | 190 | NO
| NG | 23 | 24 | 24 | 2 | 205.8 | 0.8 | 50 | 76.2 | 8 | 76.2 | 11.1 | 190 | 226.8 | 190 | NO
| NG | 10 | 7 | 7 | 2 | 123.1 | 11.57 | 50 | 76.2 | 8 | 27.5 |  | 221.5 | 9.3752e+77 | 221.5 | NO
10 | OK | 7 | 6 | 6 | 2 | 139.7 | 10.53 | 50 | 76.2 | 8 | 30.5 | 8 | 220.9 | 227.4 | 220.9 | YES
| NG | 7 | 9 | 9 | 2 | 148.4 | 0.78 | 50 | 76.2 | 8 | 72.7 | 11 | 191.8 | 226.8 | 191.8 | NO
| NG | 6 | 18 | 18 | 2 | 141.3 | 10.53 | 50 | 76.2 | 8 | 30.5 | 53.1 | 220.9 | 195.6 | 195.6 | NO
| NG | 18 | 47 | 47 | 2 | 167.7 | 10.38 | 50 | 76.2 | 8 | 31 | 52.4 | 220.8 | 196.4 | 196.4 | NO
| NG | 47 | 46 | 46 | 2 | 198 | 9.64 | 50 | 76.2 | 8 | 33.9 | 48.8 | 220.2 | 199.3 | 199.3 | NO
| NG | 46 | 45 | 45 | 2 | 222.5 | 9.53 | 50 | 76.2 | 8 | 34.3 | 48.2 | 220.1 | 200.2 | 200.2 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 57-940909
TR_B (available) | 65-009975
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 76.2
TR_B Baseline Loading% | 8
Total Scenarios Evaluated | 34
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 40
Switch Child Node | 10
Tie Node (TR_A side) | 10
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 121.9
Load Transferred (kW) | 11.57
TR_A Loading After (%) | 27.5
TR_B Loading After (%) | 9
Minimum Voltage (V) | 221.5