## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 41 | 0 | 0 | 21 | 54.4 | 9.31 | 50 | 71.1 | 55.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 41 | 40 | 31 | 21 | 8.9 | 21.22 | 50 | 71.1 | 55.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 0 | 1 | 1 | 21 | 91.8 | 8.32 | 50 | 71.1 | 55.4 | 51.7 | 59.7 | 215.2 | 199.4 | 199.4 | NO
| NG | 40 | 31 | 31 | 21 | 8.9 | 21.22 | 50 | 71.1 | 55.4 | 21.6 | 66.9 | 222.3 | 183.2 | 183.2 | NO
| NG | 1 | 2 | 2 | 21 | 141.5 | 6.42 | 50 | 71.1 | 55.4 | 56.1 | 58.7 | 214.2 | 204.5 | 204.5 | NO
| NG | 31 | 32 | 32 | 21 | 11.5 | 21.22 | 50 | 71.1 | 55.4 | 21.6 | 66.8 | 222.3 | 183.6 | 183.6 | NO
| NG | 32 | 33 | 33 | 21 | 21.5 | 21.22 | 50 | 71.1 | 55.4 | 21.6 | 66.8 | 222.3 | 183.9 | 183.9 | NO
| NG | 33 | 7 | 7 | 21 | 28.9 | 20.94 | 50 | 71.1 | 55.4 | 22.2 | 66.7 | 222.3 | 183.8 | 183.8 | NO
| NG | 7 | 10 | 10 | 21 | 61.3 | 6.37 | 50 | 71.1 | 55.4 | 56.1 | 58.6 | 215.6 | 207.4 | 207.4 | NO
| NG | 7 | 8 | 8 | 21 | 60.7 | 14.57 | 50 | 71.1 | 55.4 | 36.9 | 62.9 | 220.1 | 196.1 | 196.1 | NO
1 | OK | 10 | 11 | 11 | 21 | 98.6 | 3.13 | 50 | 71.1 | 55.4 | 63.7 | 57 | 214.5 | 210.8 | 210.8 | YES
| NG | 8 | 9 | 14 | 21 | 96.7 | 13.15 | 50 | 71.1 | 55.4 | 40.2 | 62.2 | 219.9 | 196.5 | 196.5 | NO
2 | ** OPTIMAL ** | 11 | 36 | 36 | 21 | 148 | 2.25 | 50 | 71.1 | 55.4 | 65.7 | 56.5 | 213.8 | 212.3 | 212.3 | YES
| NG | 9 | 16 | 16 | 21 | 100 | 11.1 | 50 | 71.1 | 55.4 | 44.4 | 61.1 | 219.3 | 200.9 | 200.9 | NO
3 | OK | 9 | 14 | 14 | 21 | 96.7 | 1.8 | 50 | 71.1 | 55.4 | 66.8 | 56.3 | 213.2 | 212.3 | 212.3 | YES
| NG | 16 | 17 | 17 | 21 | 136.3 | 10.92 | 50 | 71.1 | 55.4 | 45.3 | 61 | 219.2 | 200.9 | 200.9 | NO
4 | OK | 14 | 15 | 15 | 21 | 100.5 | 1.32 | 50 | 71.1 | 55.4 | 67.9 | 56 | 213.3 | 212.3 | 212.3 | YES
5 | OK | 15 | 18 | 18 | 21 | 118.8 | 0.21 | 50 | 71.1 | 55.4 | 70.6 | 55.5 | 212 | 212.3 | 212 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-001564
TR_B (available) | 66-016835
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 71.1
TR_B Baseline Loading% | 55.4
Total Scenarios Evaluated | 18
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 36
Tie Node (TR_A side) | 36
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 148
Load Transferred (kW) | 2.25
TR_A Loading After (%) | 65.7
TR_B Loading After (%) | 56.5
Minimum Voltage (V) | 212.3