## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 26 | 30 | 55 | 37.4 | 15.08 | 50 | 85.2 | 41.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 26 | 12 | 30 | 55 | 37.4 | 14.47 | 50 | 85.2 | 41.3 | 26.3 | 86.1 | 221.4 | 155 | 155 | NO
| NG | 12 | 13 | 30 | 55 | 37.4 | 14.16 | 50 | 85.2 | 41.3 | 27.5 | 84.5 | 221.2 | 158.1 | 158.1 | NO
| NG | 13 | 10 | 30 | 55 | 37.4 | 12.02 | 50 | 85.2 | 41.3 | 35.7 | 75.1 | 219.6 | 176.3 | 176.3 | NO
| NG | 10 | 11 | 30 | 55 | 37.4 | 9.75 | 50 | 85.2 | 41.3 | 44.4 | 67.1 | 217.9 | 190.8 | 190.8 | NO
| NG | 11 | 6 | 30 | 55 | 37.4 | 9.39 | 50 | 85.2 | 41.3 | 45.8 | 66 | 217.6 | 192.7 | 192.7 | NO
| NG | 6 | 7 | 30 | 55 | 37.4 | 8.91 | 50 | 85.2 | 41.3 | 47.7 | 64.5 | 217.2 | 195.1 | 195.1 | NO
| NG | 7 | 8 | 30 | 55 | 37.4 | 8.4 | 50 | 85.2 | 41.3 | 49.7 | 63 | 216.8 | 197.6 | 197.6 | NO
| NG | 8 | 9 | 30 | 55 | 37.4 | 7.45 | 50 | 85.2 | 41.3 | 53.5 | 60.2 | 216.1 | 202.1 | 202.1 | NO
| NG | 9 | 23 | 30 | 55 | 37.4 | 6.87 | 50 | 85.2 | 41.3 | 55.8 | 58.6 | 215.4 | 204.6 | 204.6 | NO
| NG | 23 | 22 | 30 | 55 | 37.4 | 6.14 | 50 | 85.2 | 41.3 | 58.7 | 56.5 | 213.9 | 207.7 | 207.7 | NO
| NG | 22 | 3 | 30 | 55 | 37.4 | 5.49 | 50 | 85.2 | 41.3 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
1 | ** OPTIMAL ** | 3 | 2 | 30 | 55 | 37.4 | 5.21 | 50 | 85.2 | 41.3 | 62.5 | 53.8 | 211.8 | 211.7 | 211.7 | YES
2 | OK | 2 | 35 | 30 | 55 | 37.4 | 5.21 | 50 | 85.2 | 41.3 | 62.5 | 53.8 | 211.8 | 211.7 | 211.7 | YES
3 | OK | 35 | 34 | 30 | 55 | 37.4 | 5.1 | 50 | 85.2 | 41.3 | 62.9 | 53.8 | 211.5 | 211.7 | 211.5 | YES
4 | OK | 34 | 31 | 30 | 55 | 37.4 | 4.69 | 50 | 85.2 | 41.3 | 64.6 | 52.7 | 210.4 | 213.1 | 210.4 | YES
| NG | 31 | 30 | 30 | 55 | 37.4 | 2.41 | 50 | 85.2 | 41.3 | 74.3 | 47 | 203.2 | 219.9 | 203.2 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 58-002911
TR_B (available) | 57-008366
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 85.2
TR_B Baseline Loading% | 41.3
Total Scenarios Evaluated | 17
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 3
Switch Child Node | 2
Tie Node (TR_A side) | 30
Tie Node (TR_B side) | 55
Tie Line Distance (m) | 37.4
Load Transferred (kW) | 5.21
TR_A Loading After (%) | 62.5
TR_B Loading After (%) | 53.8
Minimum Voltage (V) | 211.7