## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 48 | 19 | 58 | 153 | 13.9 | 11.71 | 50 | 80.4 | 46.9 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 19 | 18 | 17 | 153 | 146.6 | 0.53 | 50 | 80.4 | 46.9 | 78.4 | 47.3 | 213.2 | 210.8 | 210.8 | YES
| NG | 19 | 10 | 58 | 153 | 13.9 | 11.18 | 50 | 80.4 | 46.9 | 36.8 | 55.9 | 215.8 | 197.7 | 197.7 | NO
2 | OK | 18 | 16 | 17 | 153 | 146.6 | 0.2 | 50 | 80.4 | 46.9 | 79.6 | 47.1 | 212.9 | 210.9 | 210.9 | YES
3 | OK | 10 | 27 | 58 | 153 | 13.9 | 0.4 | 50 | 80.4 | 46.9 | 78.8 | 47.2 | 212.8 | 210.9 | 210.9 | YES
4 | ** OPTIMAL ** | 27 | 46 | 58 | 153 | 13.9 | 0.3 | 50 | 80.4 | 46.9 | 79.2 | 47.2 | 212.7 | 210.9 | 210.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-004385
TR_B (available) | 37-016125
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 80.4
TR_B Baseline Loading% | 46.9
Total Scenarios Evaluated | 6
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 27
Switch Child Node | 46
Tie Node (TR_A side) | 58
Tie Node (TR_B side) | 153
Tie Line Distance (m) | 13.9
Load Transferred (kW) | 0.3
TR_A Loading After (%) | 79.2
TR_B Loading After (%) | 47.2
Minimum Voltage (V) | 210.9