## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 23 | 42 | 10 | 6.1 | 12.38 | 50 | 86.5 | 13.9 | 38.4 | 49.4 | 222.3 | 205.8 | 205.8 | NO
| NG | 23 | 24 | 42 | 10 | 6.1 | 10.39 | 50 | 86.5 | 13.9 | 46 | 42.5 | 221.2 | 209.8 | 209.8 | NO
| NG | 24 | 35 | 42 | 10 | 6.1 | 10.04 | 50 | 86.5 | 13.9 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 13.9% (degenerate)
1 | OK | 35 | 45 | 42 | 10 | 6.1 | 9.41 | 50 | 86.5 | 13.9 | 49.8 | 39.3 | 220.6 | 211.6 | 211.6 | YES
2 | OK | 45 | 22 | 42 | 10 | 6.1 | 9.41 | 50 | 86.5 | 13.9 | 49.8 | 39.3 | 220.6 | 211.6 | 211.6 | YES
3 | OK | 22 | 21 | 42 | 10 | 6.1 | 7.99 | 50 | 86.5 | 13.9 | 55.2 | 35.8 | 220 | 213.6 | 213.6 | YES
4 | OK | 21 | 20 | 42 | 10 | 6.1 | 7.26 | 50 | 86.5 | 13.9 | 58 | 32.8 | 219.4 | 215.2 | 215.2 | YES
5 | OK | 20 | 8 | 42 | 10 | 6.1 | 7.26 | 50 | 86.5 | 13.9 | 58 | 32.8 | 219.4 | 215.2 | 215.2 | YES
6 | OK | 8 | 28 | 30 | 7 | 108.1 | 4.61 | 50 | 86.5 | 13.9 | 68.2 | 32.2 | 219.5 | 215.9 | 215.9 | YES
7 | OK | 28 | 29 | 30 | 7 | 108.1 | 4.19 | 50 | 86.5 | 13.9 | 69.9 | 30.5 | 219.1 | 216.9 | 216.9 | YES
8 | OK | 29 | 30 | 30 | 7 | 108.1 | 4.19 | 50 | 86.5 | 13.9 | 69.9 | 30.5 | 219.1 | 216.9 | 216.9 | YES
9 | ** OPTIMAL ** | 30 | 33 | 33 | 7 | 114.5 | 2.75 | 50 | 86.5 | 13.9 | 75.5 | 24.7 | 217.8 | 220.3 | 217.8 | YES
10 | OK | 33 | 34 | 34 | 7 | 131.8 | 2.02 | 50 | 86.5 | 13.9 | 78.4 | 21.8 | 217.2 | 222 | 217.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-005281
TR_B (available) | 64-007376
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 86.5
TR_B Baseline Loading% | 13.9
Total Scenarios Evaluated | 13
Feasible Scenarios | 10
--- Optimal Solution ---
Switch Parent Node | 30
Switch Child Node | 33
Tie Node (TR_A side) | 33
Tie Node (TR_B side) | 7
Tie Line Distance (m) | 114.5
Load Transferred (kW) | 2.75
TR_A Loading After (%) | 75.5
TR_B Loading After (%) | 24.7
Minimum Voltage (V) | 217.8