## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 3 | 11 | 13 | 47 | 14.1 | 3.46 | 50 | 84.3 | 52.9 | 71 | 62.9 | 215.3 | 211.9 | 211.9 | YES
2 | ** OPTIMAL ** | 11 | 6 | 13 | 47 | 14.1 | 1.31 | 50 | 84.3 | 52.9 | 79.2 | 54.6 | 215.4 | 213.7 | 213.7 | YES
| NG | 24 | 25 | 34 | 30 | 52.1 | 6.04 | 50 | 84.3 | 52.9 | 60.5 | 78.6 | 221.7 | 196.6 | 196.6 | NO
3 | OK | 24 | 23 | 41 | 11 | 40.3 | 1.41 | 50 | 84.3 | 52.9 | 78.7 | 58.5 | 216.1 | 212.5 | 212.5 | YES
4 | OK | 24 | 35 | 37 | 0 | 19.3 | 1.36 | 50 | 84.3 | 52.9 | 78.9 | 58.2 | 216 | 212.9 | 212.9 | YES
| NG | 25 | 26 | 34 | 30 | 52.1 | 5.88 | 50 | 84.3 | 52.9 | 61.1 | 77.8 | 221.7 | 197.2 | 197.2 | NO
| NG | 0 | 1 | 1 | 11 | 32.8 | 6.84 | 50 | 84.3 | 52.9 | 57.8 | 65.3 | 217.5 | 208.7 | 208.7 | NO
5 | OK | 0 | 21 | 21 | 11 | 49.2 | 1.47 | 50 | 84.3 | 52.9 | 78.6 | 58.8 | 214.5 | 212.4 | 212.4 | YES
| NG | 26 | 27 | 34 | 30 | 52.1 | 5.88 | 50 | 84.3 | 52.9 | 61.1 | 76 | 221.7 | 198.7 | 198.7 | NO
| NG | 1 | 10 | 10 | 11 | 73.5 | 6.73 | 50 | 84.3 | 52.9 | 58.2 | 65.3 | 217.4 | 208.7 | 208.7 | NO
| NG | 27 | 39 | 34 | 30 | 52.1 | 5.49 | 50 | 84.3 | 52.9 | 62.6 | 76 | 221.7 | 198.7 | 198.7 | NO
| NG | 10 | 8 | 8 | 11 | 111.2 | 6.4 | 50 | 84.3 | 52.9 | 59.4 | 65.3 | 217.2 | 208.7 | 208.7 | NO
| NG | 39 | 40 | 34 | 30 | 52.1 | 5.41 | 50 | 84.3 | 52.9 | 63 | 75.7 | 221.7 | 199 | 199 | NO
| NG | 8 | 9 | 9 | 11 | 133.9 | 6.27 | 50 | 84.3 | 52.9 | 59.9 | 64.8 | 217.2 | 209 | 209 | NO
| NG | 40 | 28 | 34 | 30 | 52.1 | 5.35 | 50 | 84.3 | 52.9 | 63.2 | 75.4 | 221.6 | 199.2 | 199.2 | NO
| NG | 28 | 29 | 30 | 11 | 136.5 | 4.56 | 50 | 84.3 | 52.9 | 66.2 | 71.7 | 221 | 204.7 | 204.7 | NO
6 | OK | 29 | 30 | 30 | 11 | 136.5 | 1.31 | 50 | 84.3 | 52.9 | 79 | 58.1 | 216.8 | 212.6 | 212.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-005535
TR_B (available) | 60-020450
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 84.3
TR_B Baseline Loading% | 52.9
Total Scenarios Evaluated | 17
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 6
Tie Node (TR_A side) | 13
Tie Node (TR_B side) | 47
Tie Line Distance (m) | 14.1
Load Transferred (kW) | 1.31
TR_A Loading After (%) | 79.2
TR_B Loading After (%) | 54.6
Minimum Voltage (V) | 213.7