## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 25 | 13 | 7 | 21 | 8.1 | 7.72 | 50 | 22.2 | 20 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 13 | 14 | 7 | 21 | 8.1 | 7.72 | 50 | 22.2 | 20 | 4.4 | 29 | 230 | 223 | 223 | YES
2 | OK | 14 | 23 | 7 | 21 | 8.1 | 7.72 | 50 | 22.2 | 20 | 4.4 | 29 | 230 | 223 | 223 | YES
3 | OK | 23 | 9 | 7 | 21 | 8.1 | 7.72 | 50 | 22.2 | 20 | 4.4 | 29 | 230 | 223 | 223 | YES
4 | OK | 9 | 10 | 7 | 21 | 8.1 | 7.7 | 50 | 22.2 | 20 | 4.4 | 29 | 230 | 223 | 223 | YES
5 | OK | 10 | 21 | 7 | 21 | 8.1 | 6.54 | 50 | 22.2 | 20 | 6.6 | 27.6 | 229.9 | 223.1 | 223.1 | YES
6 | OK | 21 | 22 | 7 | 21 | 8.1 | 5.88 | 50 | 22.2 | 20 | 6.6 | 26.8 | 229.9 | 223 | 223 | YES
7 | OK | 22 | 17 | 7 | 21 | 8.1 | 5.88 | 50 | 22.2 | 20 | 8.6 | 26.8 | 229.7 | 223 | 223 | YES
8 | ** OPTIMAL ** | 17 | 18 | 7 | 21 | 8.1 | 3.32 | 50 | 22.2 | 20 | 14.5 | 23.9 | 228.4 | 223.5 | 223.5 | YES
9 | OK | 18 | 0 | 7 | 21 | 8.1 | 3.32 | 50 | 22.2 | 20 | 14.5 | 23.9 | 228.4 | 223.5 | 223.5 | YES
10 | OK | 0 | 1 | 7 | 21 | 8.1 | 0.77 | 50 | 22.2 | 20 | 20.4 | 20.9 | 226.8 | 223.5 | 223.5 | YES
11 | OK | 1 | 8 | 7 | 21 | 8.1 | 0.17 | 50 | 22.2 | 20 | 21.8 | 20.2 | 226.9 | 223.5 | 223.5 | YES
12 | OK | 8 | 6 | 7 | 21 | 8.1 | 0.17 | 50 | 22.2 | 20 | 21.8 | 20.2 | 226.9 | 223.5 | 223.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-009656
TR_B (available) | 67-033545
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 22.2
TR_B Baseline Loading% | 20
Total Scenarios Evaluated | 13
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 18
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 8.1
Load Transferred (kW) | 3.32
TR_A Loading After (%) | 14.5
TR_B Loading After (%) | 23.9
Minimum Voltage (V) | 223.5