## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 42 | 62 | 65 | 1.4 | 17.93 | 50 | 73.7 | 35.7 | 28.1 | 51.8 | 216.7 | 179.2 | 179.2 | NO
| NG | 50 | 48 | 48 | 66 | 149 | 18.73 | 50 | 73.7 | 35.7 | 51.6 | 42.3 | 197.5 | 194.8 | 194.8 | NO
1 | OK | 50 | 82 | 83 | 66 | 82.9 | 24.81 | 50 | 73.7 | 35.7 | 43 | 39.6 | 216 | 211.5 | 211.5 | YES
| NG | 42 | 43 | 62 | 65 | 1.4 | 17.24 | 50 | 73.7 | 35.7 | 29.4 | 51 | 216.6 | 181.5 | 181.5 | NO
| NG | 42 | 51 | 51 | 66 | 114.2 | 0.69 | 50 | 73.7 | 35.7 | 72.3 | 36.2 | 196.3 | 212.5 | 196.3 | NO
2 | OK | 82 | 83 | 83 | 66 | 82.9 | 24.35 | 50 | 73.7 | 35.7 | 43.6 | 39.6 | 215.9 | 211.5 | 211.5 | YES
| NG | 82 | 87 | 87 | 66 | 110.6 | 0.46 | 50 | 73.7 | 35.7 | 73.2 | 35.7 | 196 | 212.6 | 196 | NO
| NG | 43 | 44 | 62 | 65 | 1.4 | 16.87 | 50 | 73.7 | 35.7 | 29.8 | 50.6 | 216.6 | 182.8 | 182.8 | NO
| NG | 51 | 52 | 52 | 66 | 119.1 | 0.38 | 50 | 73.7 | 35.7 | 72.7 | 36 | 196.1 | 212.6 | 196.1 | NO
3 | OK | 83 | 96 | 96 | 66 | 95.5 | 24.35 | 50 | 73.7 | 35.7 | 43.6 | 39.6 | 215.9 | 211.9 | 211.9 | YES
| NG | 87 | 88 | 88 | 66 | 117.5 | 0.46 | 50 | 73.7 | 35.7 | 73.2 | 35.7 | 196 | 212.6 | 196 | NO
4 | OK | 44 | 16 | 19 | 66 | 74.6 | 5.08 | 50 | 73.7 | 35.7 | 43.7 | 39.6 | 215.3 | 211.9 | 211.9 | YES
| NG | 44 | 59 | 62 | 65 | 1.4 | 11.79 | 50 | 73.7 | 35.7 | 59.6 | 45.4 | 197 | 197.8 | 197 | NO
5 | OK | 96 | 92 | 92 | 66 | 126.7 | 23.6 | 50 | 73.7 | 35.7 | 44.4 | 39.6 | 215.8 | 211.9 | 211.9 | YES
6 | OK | 16 | 12 | 19 | 66 | 74.6 | 5.08 | 50 | 73.7 | 35.7 | 44.6 | 39.6 | 215.1 | 211.9 | 211.9 | YES
| NG | 59 | 60 | 62 | 65 | 1.4 | 11.79 | 50 | 73.7 | 35.7 | 59.6 | 45.4 | 197 | 197.8 | 197 | NO
7 | OK | 12 | 13 | 19 | 66 | 74.6 | 2.94 | 50 | 73.7 | 35.7 | 47 | 37.9 | 215 | 212.2 | 212.2 | YES
| NG | 12 | 17 | 17 | 66 | 116.4 | 2.14 | 50 | 73.7 | 35.7 | 71.1 | 36.1 | 196.8 | 212.5 | 196.8 | NO
| NG | 60 | 61 | 36 | 26 | 68.8 | 11.79 | 50 | 73.7 | 35.7 | 59.6 | 36.8 | 197 | 212.6 | 197 | NO
8 | OK | 13 | 14 | 19 | 66 | 74.6 | 2.94 | 50 | 73.7 | 35.7 | 47 | 37.8 | 215 | 212.2 | 212.2 | YES
| NG | 17 | 18 | 18 | 66 | 118.6 | 1.16 | 50 | 73.7 | 35.7 | 72.3 | 35.7 | 195.9 | 212.6 | 195.9 | NO
| NG | 61 | 33 | 36 | 26 | 68.8 | 2.62 | 50 | 73.7 | 35.7 | 70.6 | 36.4 | 196.9 | 212.6 | 196.9 | NO
9 | ** OPTIMAL ** | 14 | 15 | 15 | 66 | 126.6 | 1.27 | 50 | 73.7 | 35.7 | 49 | 35.7 | 215 | 212.6 | 212.6 | YES
| NG | 14 | 57 | 19 | 66 | 74.6 | 1.53 | 50 | 73.7 | 35.7 | 71.9 | 36.8 | 195.9 | 212.4 | 195.9 | NO
| NG | 33 | 34 | 36 | 26 | 68.8 | 1.27 | 50 | 73.7 | 35.7 | 72.2 | 36 | 196.4 | 212.6 | 196.4 | NO
| NG | 57 | 19 | 19 | 66 | 74.6 | 1.33 | 50 | 73.7 | 35.7 | 72.1 | 36.7 | 195.9 | 212.4 | 195.9 | NO
| NG | 34 | 35 | 36 | 26 | 68.8 | 0.96 | 50 | 73.7 | 35.7 | 72.5 | 35.7 | 196.4 | 212.6 | 196.4 | NO
| NG | 19 | 20 | 20 | 66 | 75.1 | 0.39 | 50 | 73.7 | 35.7 | 73.2 | 29.6 | 196 | 8.5 | 8.5 | NO
| NG | 35 | 36 | 36 | 26 | 68.8 | 0.3 | 50 | 73.7 | 35.7 | 73.3 | 35.7 | 196 | 212.6 | 196 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 58-013417
TR_B (available) | 63-022807
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 73.7
TR_B Baseline Loading% | 35.7
Total Scenarios Evaluated | 29
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 14
Switch Child Node | 15
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 66
Tie Line Distance (m) | 126.6
Load Transferred (kW) | 1.27
TR_A Loading After (%) | 49
TR_B Loading After (%) | 35.7
Minimum Voltage (V) | 212.6