## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 42 | 36 | 0 | 185.1 | 17.93 | 50 | 73.7 | 23.2 | 28.1 | 46.6 | 216.7 | 188.5 | 188.5 | NO
1 | OK | 50 | 82 | 86 | 22 | 175 | 24.81 | 50 | 73.7 | 23.2 | 43 | 29.5 | 216 | 210.2 | 210.2 | YES
| NG | 42 | 43 | 36 | 0 | 185.1 | 17.24 | 50 | 73.7 | 23.2 | 29.4 | 45.7 | 216.6 | 188.2 | 188.2 | NO
2 | OK | 82 | 83 | 86 | 22 | 175 | 24.35 | 50 | 73.7 | 23.2 | 43.6 | 29.5 | 215.9 | 210.2 | 210.2 | YES
| NG | 43 | 44 | 36 | 0 | 185.1 | 16.87 | 50 | 73.7 | 23.2 | 29.8 | 45.2 | 216.6 | 188.7 | 188.7 | NO
3 | OK | 83 | 96 | 86 | 22 | 175 | 24.35 | 50 | 73.7 | 23.2 | 43.6 | 29.5 | 215.9 | 210.2 | 210.2 | YES
| NG | 44 | 59 | 36 | 0 | 185.1 | 11.79 | 50 | 73.7 | 23.2 | 59.6 | 39 | 197 | 189.6 | 189.6 | NO
4 | OK | 96 | 92 | 86 | 22 | 175 | 23.6 | 50 | 73.7 | 23.2 | 44.4 | 29.5 | 215.8 | 210.2 | 210.2 | YES
| NG | 59 | 60 | 36 | 0 | 185.1 | 11.79 | 50 | 73.7 | 23.2 | 59.6 | 39 | 197 | 189.6 | 189.6 | NO
5 | OK | 92 | 93 | 86 | 22 | 175 | 22.08 | 50 | 73.7 | 23.2 | 46.2 | 29.5 | 215.8 | 210.2 | 210.2 | YES
| NG | 60 | 61 | 36 | 0 | 185.1 | 11.79 | 50 | 73.7 | 23.2 | 59.6 | 39 | 197 | 189.6 | 189.6 | NO
6 | OK | 93 | 24 | 86 | 22 | 175 | 22.08 | 50 | 73.7 | 23.2 | 46.2 | 29.5 | 215.8 | 210.2 | 210.2 | YES
| NG | 61 | 33 | 36 | 0 | 185.1 | 2.62 | 50 | 73.7 | 23.2 | 70.6 | 26.2 | 196.9 | 214 | 196.9 | NO
7 | ** OPTIMAL ** | 24 | 26 | 86 | 22 | 175 | 17.72 | 50 | 73.7 | 23.2 | 50.6 | 26.5 | 215.3 | 214.2 | 214.2 | YES
| NG | 33 | 34 | 36 | 0 | 185.1 | 1.27 | 50 | 73.7 | 23.2 | 72.2 | 24.6 | 196.4 | 214.1 | 196.4 | NO
8 | OK | 26 | 29 | 86 | 22 | 175 | 17.72 | 50 | 73.7 | 23.2 | 51.3 | 26.5 | 215.3 | 214.2 | 214.2 | YES
| NG | 34 | 35 | 36 | 0 | 185.1 | 0.96 | 50 | 73.7 | 23.2 | 72.5 | 24.3 | 196.4 | 214.2 | 196.4 | NO
| NG | 29 | 30 | 99 | 22 | 176.7 | 14.49 | 50 | 73.7 | 23.2 | 30.2 | 28 | 6.1 | 208.7 | 6.1 | NO
| NG | 29 | 84 | 86 | 22 | 175 | 0.88 | 50 | 73.7 | 23.2 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 23.2% (degenerate)
| NG | 35 | 36 | 36 | 0 | 185.1 | 0.3 | 50 | 73.7 | 23.2 | 73.3 | 23.2 | 196 | 214.2 | 196 | NO
| NG | 30 | 31 | 99 | 22 | 176.7 | 14.2 | 50 | 73.7 | 23.2 | 60.9 | 27.7 | 6.1 | 208.6 | 6.1 | NO
| NG | 84 | 85 | 86 | 22 | 175 | 0.63 | 50 | 73.7 | 23.2 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 23.2% (degenerate)
| NG | 31 | 32 | 99 | 22 | 176.7 | 13.77 | 50 | 73.7 | 23.2 | 0 | 27.1 | 5.5 | 210.7 | 5.5 | NO
| NG | 85 | 86 | 86 | 22 | 175 | 0.63 | 50 | 73.7 | 23.2 | 72.8 |  | 197 | 6 | 6 | NO
| NG | 32 | 72 | 99 | 22 | 176.7 | 13.77 | 50 | 73.7 | 23.2 | 0 | 27.1 | 7.3 | 210.7 | 7.3 | NO
| NG | 72 | 66 | 99 | 22 | 176.7 | 13.77 | 50 | 73.7 | 23.2 | 3.4 | 26.7 | 7.3 | 210.7 | 7.3 | NO
| NG | 66 | 67 | 99 | 22 | 176.7 | 10.79 | 50 | 73.7 | 23.2 | 0 | 26.7 | 86.5 | 210.7 | 86.5 | NO
| NG | 67 | 75 | 99 | 22 | 176.7 | 10.31 | 50 | 73.7 | 23.2 | 0 | 26.2 | 6.8 | 210.9 | 6.8 | NO
9 | OK | 75 | 76 | 99 | 22 | 176.7 | 9.2 | 50 | 73.7 | 23.2 | 0 | 24.8 | 326.6 | 213 | 213 | YES
| NG | 76 | 77 | 99 | 22 | 176.7 | 9.2 | 50 | 73.7 | 23.2 | [5 empty] | NO | TR_A sim: loading 19628289% (degenerate)
| NG | 77 | 78 | 99 | 22 | 176.7 | 8.4 | 50 | 73.7 | 23.2 | 0 | 23.9 | 0 | 212.9 | 0 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 58-013417
TR_B (available) | 65-005083
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 73.7
TR_B Baseline Loading% | 23.2
Total Scenarios Evaluated | 31
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 24
Switch Child Node | 26
Tie Node (TR_A side) | 86
Tie Node (TR_B side) | 22
Tie Line Distance (m) | 175
Load Transferred (kW) | 17.72
TR_A Loading After (%) | 50.6
TR_B Loading After (%) | 26.5
Minimum Voltage (V) | 214.2