## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 29 | 47 | 13 | 7.1 | 27.02 | 50 | 67.7 | 23.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 29 | 5 | 47 | 13 | 7.1 | 24.19 | 50 | 67.7 | 23.4 | 39.9 | 41.6 | 221.8 | 210.2 | 210.2 | YES
2 | OK | 5 | 4 | 47 | 13 | 7.1 | 13.64 | 50 | 67.7 | 23.4 | 52 | 33.4 | 221.8 | 223.7 | 221.8 | YES
3 | OK | 4 | 6 | 47 | 13 | 7.1 | 12.23 | 50 | 67.7 | 23.4 | 53.6 | 32.3 | 221.8 | 223.7 | 221.8 | YES
4 | OK | 6 | 8 | 47 | 13 | 7.1 | 12.22 | 50 | 67.7 | 23.4 | 53.6 | 32.3 | 221.8 | 223.7 | 221.8 | YES
5 | OK | 8 | 7 | 47 | 13 | 7.1 | 9.67 | 50 | 67.7 | 23.4 | 56.5 | 30.5 | 221.7 | 224.1 | 221.7 | YES
6 | OK | 7 | 9 | 47 | 13 | 7.1 | 9.33 | 50 | 67.7 | 23.4 | 56.9 | 30.2 | 221.6 | 224.1 | 221.6 | YES
| NG | 9 | 37 | 47 | 13 | 7.1 | 2.69 | 50 | 67.7 | 23.4 | 0 | 25.4 | 6.9 | 225.2 | 6.9 | NO
7 | OK | 37 | 36 | 47 | 13 | 7.1 | 0.02 | 50 | 67.7 | 23.4 | 67.7 | 23.5 | 221.2 | 225.8 | 221.2 | YES
8 | OK | 36 | 35 | 47 | 13 | 7.1 | 0.02 | 50 | 67.7 | 23.4 | 67.7 | 23.5 | 221.2 | 225.8 | 221.2 | YES
9 | ** OPTIMAL ** | 35 | 48 | 47 | 13 | 7.1 | 0.02 | 50 | 67.7 | 23.4 | 0 | 23.5 | 227 | 225.8 | 225.8 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-015157
TR_B (available) | 43-005278
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 67.7
TR_B Baseline Loading% | 23.4
Total Scenarios Evaluated | 11
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 35
Switch Child Node | 48
Tie Node (TR_A side) | 47
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 7.1
Load Transferred (kW) | 0.02
TR_A Loading After (%) | 0
TR_B Loading After (%) | 23.5
Minimum Voltage (V) | 225.8