## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 26 | 0 | 18 | 0.7 | 31.58 | 95 | 67.7 | 36.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 26 | 27 | 0 | 18 | 0.7 | 29.04 | 95 | 67.7 | 36.7 | 34 | 70.4 | 225.8 | 221 | 221 | YES
2 | OK | 27 | 41 | 0 | 18 | 0.7 | 27.84 | 95 | 67.7 | 36.7 | 35.4 | 68.9 | 225.8 | 220.8 | 220.8 | YES
3 | OK | 41 | 22 | 0 | 18 | 0.7 | 27.84 | 95 | 67.7 | 36.7 | 35.4 | 68.9 | 225.8 | 220.8 | 220.8 | YES
4 | OK | 22 | 23 | 0 | 18 | 0.7 | 26.95 | 95 | 67.7 | 36.7 | 36.4 | 67.9 | 225.8 | 220.8 | 220.8 | YES
5 | OK | 23 | 32 | 0 | 18 | 0.7 | 24.93 | 95 | 67.7 | 36.7 | 38.7 | 65.6 | 225.8 | 220.8 | 220.8 | YES
6 | OK | 32 | 33 | 0 | 18 | 0.7 | 24.93 | 95 | 67.7 | 36.7 | 38.7 | 65.6 | 225.8 | 220.8 | 220.8 | YES
7 | OK | 33 | 2 | 0 | 18 | 0.7 | 20.89 | 95 | 67.7 | 36.7 | 43.3 | 60.9 | 225.3 | 221.8 | 221.8 | YES
8 | OK | 2 | 3 | 0 | 18 | 0.7 | 5.07 | 95 | 67.7 | 36.7 | 61.8 | 42.5 | 222.3 | 225.3 | 222.3 | YES
9 | ** OPTIMAL ** | 2 | 17 | 19 | 18 | 103.8 | 15.82 | 50 | 67.7 | 36.7 | 49.2 | 55 | 224.8 | 222.9 | 222.9 | YES
10 | OK | 3 | 16 | 0 | 18 | 0.7 | 4.62 | 95 | 67.7 | 36.7 | 62.3 | 41.9 | 222.3 | 225.3 | 222.3 | YES
11 | OK | 17 | 19 | 19 | 18 | 103.8 | 14.64 | 50 | 67.7 | 36.7 | 50.5 | 53.6 | 224.8 | 222.8 | 222.8 | YES
12 | OK | 16 | 14 | 0 | 18 | 0.7 | 4.26 | 95 | 67.7 | 36.7 | 62.7 | 41.5 | 222.3 | 225.3 | 222.3 | YES
13 | OK | 19 | 18 | 18 | 18 | 106.6 | 5.82 | 50 | 67.7 | 36.7 | 60.8 | 43.4 | 222.8 | 224.8 | 222.8 | YES
14 | OK | 19 | 11 | 11 | 18 | 122.2 | 3.94 | 50 | 67.7 | 36.7 | 63.1 | 41.2 | 221.2 | 225.2 | 221.2 | YES
15 | OK | 14 | 13 | 0 | 18 | 0.7 | 4.18 | 95 | 67.7 | 36.7 | 62.7 | 41.4 | 222.3 | 225.3 | 222.3 | YES
16 | OK | 11 | 10 | 20 | 33 | 132.7 | 2.55 | 50 | 67.7 | 36.7 | 64.7 | 39.6 | 221.4 | 224.3 | 221.4 | YES
17 | OK | 13 | 1 | 0 | 18 | 0.7 | 2.01 | 95 | 67.7 | 36.7 | 65.4 | 39 | 221.5 | 225.3 | 221.5 | YES
18 | OK | 10 | 30 | 20 | 33 | 132.7 | 1.47 | 50 | 67.7 | 36.7 | 66 | 38.4 | 221.5 | 225.7 | 221.5 | YES
19 | OK | 30 | 12 | 20 | 33 | 132.7 | 1.47 | 50 | 67.7 | 36.7 | 66 | 38.4 | 221.5 | 225.7 | 221.5 | YES
20 | OK | 12 | 51 | 20 | 33 | 132.7 | 1.47 | 50 | 67.7 | 36.7 | 66 | 38.4 | 221.5 | 225.7 | 221.5 | YES
21 | OK | 51 | 50 | 20 | 33 | 132.7 | 1.39 | 50 | 67.7 | 36.7 | 66.1 | 38.2 | 221.5 | 225.7 | 221.5 | YES
22 | OK | 50 | 21 | 20 | 33 | 132.7 | 1.07 | 50 | 67.7 | 36.7 | 66.5 | 37.7 | 221.5 | 225.7 | 221.5 | YES
23 | OK | 21 | 20 | 20 | 33 | 132.7 | 0.41 | 50 | 67.7 | 36.7 | 67.2 | 37 | 221.5 | 225.7 | 221.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-015157
TR_B (available) | 45-001050
TR_A Rated kVA | 100
TR_B Rated kVA | 100
TR_A Baseline Loading% | 67.7
TR_B Baseline Loading% | 36.7
Total Scenarios Evaluated | 24
Feasible Scenarios | 23
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 17
Tie Node (TR_A side) | 19
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 103.8
Load Transferred (kW) | 15.82
TR_A Loading After (%) | 49.2
TR_B Loading After (%) | 55
Minimum Voltage (V) | 222.9