## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 26 | 44 | 1 | 69 | 31.58 | 50 | 67.7 | 37.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 28 | 29 | 7 | 24 | 17.6 | 27.02 | 50 | 67.7 | 37.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 26 | 27 | 44 | 1 | 69 | 29.04 | 50 | 67.7 | 37.5 | 34 | 46.4 | 225.8 | 199 | 199 | NO
1 | OK | 26 | 25 | 25 | 3 | 135.9 | 1.4 | 50 | 67.7 | 37.5 | 65.7 | 38.2 | 221.1 | 219 | 219 | YES
| NG | 29 | 5 | 7 | 24 | 17.6 | 24.19 | 50 | 67.7 | 37.5 | 39.9 | 49.4 | 221.8 | 199.1 | 199.1 | NO
| NG | 27 | 41 | 44 | 1 | 69 | 27.84 | 50 | 67.7 | 37.5 | 35.4 | 46.4 | 225.8 | 199 | 199 | NO
2 | OK | 25 | 24 | 24 | 3 | 142 | 1.4 | 50 | 67.7 | 37.5 | 66.1 | 37.5 | 221.1 | 219 | 219 | YES
3 | OK | 5 | 4 | 7 | 24 | 17.6 | 13.64 | 50 | 67.7 | 37.5 | 52 | 43.5 | 221.8 | 212.2 | 212.2 | YES
| NG | 41 | 22 | 12 | 1 | 109.3 | 27.84 | 50 | 67.7 | 37.5 | 35.4 | 43.3 | 225.8 | 206.6 | 206.6 | NO
4 | OK | 4 | 6 | 7 | 24 | 17.6 | 12.23 | 50 | 67.7 | 37.5 | 53.6 | 42.8 | 221.8 | 212 | 212 | YES
| NG | 22 | 23 | 12 | 1 | 109.3 | 26.95 | 50 | 67.7 | 37.5 | 36.4 | 43.3 | 225.8 | 206.6 | 206.6 | NO
5 | OK | 6 | 8 | 7 | 24 | 17.6 | 12.22 | 50 | 67.7 | 37.5 | 53.6 | 42.8 | 221.8 | 212 | 212 | YES
| NG | 23 | 32 | 12 | 1 | 109.3 | 24.93 | 50 | 67.7 | 37.5 | 38.7 | 43.3 | 225.8 | 206.6 | 206.6 | NO
6 | OK | 8 | 7 | 7 | 24 | 17.6 | 9.67 | 50 | 67.7 | 37.5 | 56.5 | 41.9 | 221.7 | 212.8 | 212.8 | YES
| NG | 32 | 33 | 12 | 1 | 109.3 | 24.93 | 50 | 67.7 | 37.5 | 38.7 | 43.3 | 225.8 | 206.6 | 206.6 | NO
7 | OK | 7 | 9 | 9 | 24 | 34.6 | 9.33 | 50 | 67.7 | 37.5 | 56.9 | 41.8 | 221.6 | 212.7 | 212.7 | YES
8 | OK | 33 | 2 | 12 | 1 | 109.3 | 20.89 | 50 | 67.7 | 37.5 | 43.3 | 42 | 225.3 | 211.3 | 211.3 | YES
| NG | 9 | 37 | 37 | 24 | 52.5 | 2.69 | 50 | 67.7 | 37.5 | 0 | 38.5 | 6 | 219 | 6 | NO
9 | OK | 2 | 17 | 12 | 1 | 109.3 | 15.82 | 50 | 67.7 | 37.5 | 49.2 | 40.9 | 224.8 | 215.4 | 215.4 | YES
10 | OK | 37 | 36 | 36 | 52 | 69 | 0.02 | 50 | 67.7 | 37.5 | 67.7 | 37.5 | 221.2 | 219 | 219 | YES
11 | OK | 17 | 19 | 12 | 1 | 109.3 | 14.64 | 50 | 67.7 | 37.5 | 50.5 | 40.9 | 224.8 | 215.4 | 215.4 | YES
12 | OK | 36 | 35 | 53 | 52 | 71 | 0.02 | 50 | 67.7 | 37.5 | 67.7 | 37.5 | 221.2 | 219 | 219 | YES
13 | OK | 19 | 11 | 12 | 1 | 109.3 | 3.94 | 50 | 67.7 | 37.5 | 63.1 | 38.7 | 221.2 | 219.2 | 219.2 | YES
| NG | 35 | 48 | 53 | 52 | 71 | 0.02 | 50 | 67.7 | 37.5 | 50.7 | 37.5 | 6 | 219 | 6 | NO
14 | ** OPTIMAL ** | 11 | 10 | 12 | 1 | 109.3 | 2.55 | 50 | 67.7 | 37.5 | 64.7 | 38.7 | 221.4 | 219.2 | 219.2 | YES
15 | OK | 10 | 30 | 12 | 1 | 109.3 | 1.47 | 50 | 67.7 | 37.5 | 66 | 38.2 | 221.5 | 219.1 | 219.1 | YES
16 | OK | 30 | 12 | 12 | 1 | 109.3 | 1.47 | 50 | 67.7 | 37.5 | 66 | 38.2 | 221.5 | 219.1 | 219.1 | YES
17 | OK | 12 | 51 | 51 | 1 | 112.1 | 1.47 | 50 | 67.7 | 37.5 | 66 | 38.2 | 221.5 | 219.1 | 219.1 | YES
18 | OK | 51 | 50 | 50 | 1 | 116.7 | 1.39 | 50 | 67.7 | 37.5 | 66.1 | 38.1 | 221.5 | 219.1 | 219.1 | YES
19 | OK | 50 | 21 | 21 | 1 | 123.9 | 1.07 | 50 | 67.7 | 37.5 | 66.5 | 37.9 | 221.5 | 219.1 | 219.1 | YES
20 | OK | 21 | 20 | 20 | 1 | 129.5 | 0.41 | 50 | 67.7 | 37.5 | 67.2 | 37.6 | 221.5 | 219 | 219 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-015157
TR_B (available) | 64-017417
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 67.7
TR_B Baseline Loading% | 37.5
Total Scenarios Evaluated | 31
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 11
Switch Child Node | 10
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 1
Tie Line Distance (m) | 109.3
Load Transferred (kW) | 2.55
TR_A Loading After (%) | 64.7
TR_B Loading After (%) | 38.7
Minimum Voltage (V) | 219.2