## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 26 | 20 | 67 | 19.9 | 31.58 | 50 | 67.7 | 48.6 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 26 | 27 | 20 | 67 | 19.9 | 29.04 | 50 | 67.7 | 48.6 | 34 | 57 | 225.8 | 215.3 | 215.3 | YES
2 | OK | 26 | 25 | 24 | 6 | 148.2 | 1.4 | 50 | 67.7 | 48.6 | 65.7 | 49.7 | 221.1 | 215 | 215 | YES
3 | OK | 27 | 41 | 20 | 67 | 19.9 | 27.84 | 50 | 67.7 | 48.6 | 35.4 | 57 | 225.8 | 215.3 | 215.3 | YES
4 | OK | 25 | 24 | 24 | 6 | 148.2 | 1.4 | 50 | 67.7 | 48.6 | 66.1 | 48.6 | 221.1 | 215.3 | 215.3 | YES
5 | OK | 41 | 22 | 20 | 67 | 19.9 | 27.84 | 50 | 67.7 | 48.6 | 35.4 | 57 | 225.8 | 215.3 | 215.3 | YES
6 | OK | 22 | 23 | 20 | 67 | 19.9 | 26.95 | 50 | 67.7 | 48.6 | 36.4 | 57 | 225.8 | 215.3 | 215.3 | YES
7 | OK | 23 | 32 | 20 | 67 | 19.9 | 24.93 | 50 | 67.7 | 48.6 | 38.7 | 57 | 225.8 | 215.3 | 215.3 | YES
8 | OK | 32 | 33 | 20 | 67 | 19.9 | 24.93 | 50 | 67.7 | 48.6 | 38.7 | 57 | 225.8 | 215.3 | 215.3 | YES
9 | OK | 33 | 2 | 20 | 67 | 19.9 | 20.89 | 50 | 67.7 | 48.6 | 43.3 | 55.2 | 225.3 | 215.3 | 215.3 | YES
10 | OK | 2 | 3 | 0 | 49 | 36.3 | 5.07 | 50 | 67.7 | 48.6 | 61.8 | 52.4 | 222.3 | 214.5 | 214.5 | YES
11 | OK | 2 | 17 | 20 | 67 | 19.9 | 15.82 | 50 | 67.7 | 48.6 | 49.2 | 53.6 | 224.8 | 215.3 | 215.3 | YES
12 | OK | 3 | 16 | 0 | 49 | 36.3 | 4.62 | 50 | 67.7 | 48.6 | 62.3 | 52.1 | 222.3 | 214.6 | 214.6 | YES
13 | OK | 17 | 19 | 20 | 67 | 19.9 | 14.64 | 50 | 67.7 | 48.6 | 50.5 | 53.6 | 224.8 | 215.3 | 215.3 | YES
14 | OK | 16 | 14 | 0 | 49 | 36.3 | 4.26 | 50 | 67.7 | 48.6 | 62.7 | 51.8 | 222.3 | 214.6 | 214.6 | YES
15 | OK | 19 | 18 | 18 | 23 | 87.8 | 5.82 | 50 | 67.7 | 48.6 | 60.8 | 52.9 | 222.8 | 215.1 | 215.1 | YES
16 | OK | 19 | 11 | 20 | 67 | 19.9 | 3.94 | 50 | 67.7 | 48.6 | 63.1 | 50.5 | 221.2 | 215.3 | 215.3 | YES
17 | OK | 14 | 13 | 0 | 49 | 36.3 | 4.18 | 50 | 67.7 | 48.6 | 62.7 | 51.8 | 222.3 | 214.6 | 214.6 | YES
18 | OK | 11 | 10 | 20 | 67 | 19.9 | 2.55 | 50 | 67.7 | 48.6 | 64.7 | 50.5 | 221.4 | 215.3 | 215.3 | YES
19 | ** OPTIMAL ** | 13 | 1 | 0 | 49 | 36.3 | 2.01 | 50 | 67.7 | 48.6 | 65.4 | 50.1 | 221.5 | 215.3 | 215.3 | YES
20 | OK | 10 | 30 | 20 | 67 | 19.9 | 1.47 | 50 | 67.7 | 48.6 | 66 | 49.7 | 221.5 | 215.3 | 215.3 | YES
21 | OK | 30 | 12 | 20 | 67 | 19.9 | 1.47 | 50 | 67.7 | 48.6 | 66 | 49.7 | 221.5 | 215.3 | 215.3 | YES
22 | OK | 12 | 51 | 20 | 67 | 19.9 | 1.47 | 50 | 67.7 | 48.6 | 66 | 49.7 | 221.5 | 215.3 | 215.3 | YES
23 | OK | 51 | 50 | 20 | 67 | 19.9 | 1.39 | 50 | 67.7 | 48.6 | 66.1 | 49.6 | 221.5 | 215.3 | 215.3 | YES
24 | OK | 50 | 21 | 20 | 67 | 19.9 | 1.07 | 50 | 67.7 | 48.6 | 66.5 | 49.3 | 221.5 | 215.3 | 215.3 | YES
25 | OK | 21 | 20 | 20 | 67 | 19.9 | 0.41 | 50 | 67.7 | 48.6 | 67.2 | 48.8 | 221.5 | 215.3 | 215.3 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-015157
TR_B (available) | 67-006210
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 67.7
TR_B Baseline Loading% | 48.6
Total Scenarios Evaluated | 26
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 13
Switch Child Node | 1
Tie Node (TR_A side) | 0
Tie Node (TR_B side) | 49
Tie Line Distance (m) | 36.3
Load Transferred (kW) | 2.01
TR_A Loading After (%) | 65.4
TR_B Loading After (%) | 50.1
Minimum Voltage (V) | 215.3