## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 28 | 26 | 1 | 55 | 18.9 | 31.58 | 95 | 67.7 | 49.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 28 | 29 | 7 | 27 | 19.9 | 27.02 | 95 | 67.7 | 49.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 26 | 27 | 1 | 55 | 18.9 | 29.04 | 95 | 67.7 | 49.7 | 34 | 71.5 | 225.8 | 214.7 | 214.7 | YES
2 | ** OPTIMAL ** | 26 | 25 | 24 | 18 | 22.8 | 1.4 | 50 | 67.7 | 49.7 | 65.7 | 50.7 | 221.1 | 220.2 | 220.2 | YES
3 | OK | 29 | 5 | 7 | 27 | 19.9 | 24.19 | 95 | 67.7 | 49.7 | 39.9 | 68 | 221.8 | 212.8 | 212.8 | YES
4 | OK | 27 | 41 | 1 | 55 | 18.9 | 27.84 | 95 | 67.7 | 49.7 | 35.4 | 70.5 | 225.8 | 215.9 | 215.9 | YES
5 | OK | 25 | 24 | 24 | 18 | 22.8 | 1.4 | 50 | 67.7 | 49.7 | 66.1 | 49.7 | 221.1 | 220.2 | 220.2 | YES
6 | OK | 5 | 4 | 7 | 27 | 19.9 | 13.64 | 95 | 67.7 | 49.7 | 52 | 59.8 | 221.8 | 219 | 219 | YES
7 | OK | 41 | 22 | 1 | 55 | 18.9 | 27.84 | 95 | 67.7 | 49.7 | 35.4 | 70.5 | 225.8 | 215.9 | 215.9 | YES
8 | OK | 4 | 6 | 7 | 27 | 19.9 | 12.23 | 95 | 67.7 | 49.7 | 53.6 | 58.8 | 221.8 | 219 | 219 | YES
9 | OK | 22 | 23 | 1 | 55 | 18.9 | 26.95 | 95 | 67.7 | 49.7 | 36.4 | 69.8 | 225.8 | 215.9 | 215.9 | YES
10 | OK | 6 | 8 | 7 | 27 | 19.9 | 12.22 | 95 | 67.7 | 49.7 | 53.6 | 58.7 | 221.8 | 219 | 219 | YES
11 | OK | 23 | 32 | 1 | 55 | 18.9 | 24.93 | 95 | 67.7 | 49.7 | 38.7 | 68.4 | 225.8 | 215.2 | 215.2 | YES
12 | OK | 8 | 7 | 7 | 27 | 19.9 | 9.67 | 95 | 67.7 | 49.7 | 56.5 | 56.9 | 221.7 | 219.2 | 219.2 | YES
13 | OK | 32 | 33 | 1 | 55 | 18.9 | 24.93 | 95 | 67.7 | 49.7 | 38.7 | 68.4 | 225.8 | 215.2 | 215.2 | YES
14 | OK | 7 | 9 | 9 | 5 | 26.5 | 9.33 | 50 | 67.7 | 49.7 | 56.9 | 56.6 | 221.6 | 219.2 | 219.2 | YES
15 | OK | 33 | 2 | 1 | 55 | 18.9 | 20.89 | 95 | 67.7 | 49.7 | 43.3 | 65.3 | 225.3 | 214.7 | 214.7 | YES
| NG | 9 | 37 | 37 | 4 | 27.6 | 2.69 | 95 | 67.7 | 49.7 | 0 | 51.7 | 5.7 | 220.2 | 5.7 | NO
16 | OK | 2 | 3 | 1 | 55 | 18.9 | 5.07 | 95 | 67.7 | 49.7 | 61.8 | 53.4 | 222.3 | 219.8 | 219.8 | YES
17 | OK | 2 | 17 | 17 | 22 | 28.1 | 15.82 | 50 | 67.7 | 49.7 | 49.2 | 61.2 | 224.8 | 219 | 219 | YES
18 | OK | 37 | 36 | 36 | 61 | 34.6 | 0.02 | 50 | 67.7 | 49.7 | 67.7 | 49.7 | 221.2 | 220.2 | 220.2 | YES
19 | OK | 3 | 16 | 1 | 55 | 18.9 | 4.62 | 95 | 67.7 | 49.7 | 62.3 | 53.1 | 222.3 | 219.8 | 219.8 | YES
20 | OK | 17 | 19 | 19 | 22 | 56.9 | 14.64 | 50 | 67.7 | 49.7 | 50.5 | 60.4 | 224.8 | 219 | 219 | YES
21 | OK | 36 | 35 | 53 | 61 | 39.1 | 0.02 | 50 | 67.7 | 49.7 | 67.7 | 49.7 | 221.2 | 220.2 | 220.2 | YES
22 | OK | 16 | 14 | 1 | 55 | 18.9 | 4.26 | 95 | 67.7 | 49.7 | 62.7 | 52.8 | 222.3 | 219.8 | 219.8 | YES
23 | OK | 19 | 18 | 18 | 22 | 66.4 | 5.82 | 50 | 67.7 | 49.7 | 60.8 | 53.9 | 222.8 | 219.4 | 219.4 | YES
24 | OK | 19 | 11 | 11 | 22 | 93.3 | 3.94 | 50 | 67.7 | 49.7 | 63.1 | 52.6 | 221.2 | 219.7 | 219.7 | YES
| NG | 35 | 48 | 53 | 61 | 39.1 | 0.02 | 50 | 67.7 | 49.7 | 0 | 49.7 | 5.4 | 220.2 | 5.4 | NO
25 | OK | 14 | 13 | 1 | 55 | 18.9 | 4.18 | 95 | 67.7 | 49.7 | 62.7 | 52.7 | 222.3 | 219.8 | 219.8 | YES
26 | OK | 11 | 10 | 10 | 22 | 125.6 | 2.55 | 50 | 67.7 | 49.7 | 64.7 | 51.5 | 221.4 | 219.7 | 219.7 | YES
27 | OK | 13 | 1 | 1 | 55 | 18.9 | 2.01 | 95 | 67.7 | 49.7 | 65.4 | 51.1 | 221.5 | 219.8 | 219.8 | YES
28 | OK | 10 | 30 | 30 | 22 | 146 | 1.47 | 50 | 67.7 | 49.7 | 66 | 50.8 | 221.5 | 219.9 | 219.9 | YES
29 | OK | 30 | 12 | 51 | 22 | 147.8 | 1.47 | 50 | 67.7 | 49.7 | 66 | 50.8 | 221.5 | 219.9 | 219.9 | YES
30 | OK | 12 | 51 | 51 | 22 | 147.8 | 1.47 | 50 | 67.7 | 49.7 | 66 | 50.8 | 221.5 | 219.9 | 219.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-015157
TR_B (available) | 68-014462
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 67.7
TR_B Baseline Loading% | 49.7
Total Scenarios Evaluated | 34
Feasible Scenarios | 30
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 25
Tie Node (TR_A side) | 24
Tie Node (TR_B side) | 18
Tie Line Distance (m) | 22.8
Load Transferred (kW) | 1.4
TR_A Loading After (%) | 65.7
TR_B Loading After (%) | 50.7
Minimum Voltage (V) | 220.2