## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 10 | 11 | 1 | 2 | 39.1 | 18.54 | 50 | 79 | 42.5 | 35.1 | 64.6 | 220.6 | 207.1 | 207.1 | NO
1 | OK | 11 | 12 | 1 | 2 | 39.1 | 17.13 | 50 | 79 | 42.5 | 38.3 | 62.8 | 220.6 | 211.5 | 211.5 | YES
2 | OK | 12 | 8 | 1 | 2 | 39.1 | 14.6 | 50 | 79 | 42.5 | 44.1 | 59.8 | 220.6 | 211.1 | 211.1 | YES
3 | OK | 8 | 9 | 1 | 2 | 39.1 | 13.38 | 50 | 79 | 42.5 | 46.9 | 58.3 | 220.6 | 214.4 | 214.4 | YES
4 | OK | 9 | 21 | 1 | 2 | 39.1 | 10.26 | 50 | 79 | 42.5 | 54.1 | 54.6 | 219.1 | 212.8 | 212.8 | YES
5 | OK | 21 | 22 | 1 | 2 | 39.1 | 9.89 | 50 | 79 | 42.5 | 54.9 | 54.2 | 219.1 | 213.8 | 213.8 | YES
6 | OK | 22 | 40 | 1 | 2 | 39.1 | 9.35 | 50 | 79 | 42.5 | 56.2 | 53.5 | 219.1 | 215.1 | 215.1 | YES
7 | OK | 40 | 42 | 1 | 2 | 39.1 | 8.06 | 50 | 79 | 42.5 | 59.2 | 51.9 | 219.1 | 215.7 | 215.7 | YES
8 | OK | 42 | 24 | 1 | 2 | 39.1 | 6.24 | 50 | 79 | 42.5 | 63.5 | 49.7 | 219.1 | 216.1 | 216.1 | YES
9 | OK | 24 | 23 | 1 | 2 | 39.1 | 5.89 | 50 | 79 | 42.5 | 63.5 | 49.3 | 219.1 | 216.2 | 216.2 | YES
10 | OK | 23 | 34 | 1 | 2 | 39.1 | 5.89 | 50 | 79 | 42.5 | 64.3 | 49.3 | 219.1 | 216.2 | 216.2 | YES
11 | OK | 34 | 0 | 1 | 2 | 39.1 | 5.89 | 50 | 79 | 42.5 | 64.3 | 49.3 | 219.1 | 216.2 | 216.2 | YES
12 | OK | 0 | 1 | 1 | 2 | 39.1 | 5.89 | 50 | 79 | 42.5 | 64.3 | 49.3 | 219.1 | 216.2 | 216.2 | YES
13 | OK | 1 | 6 | 6 | 2 | 39.6 | 5.89 | 50 | 79 | 42.5 | 64.3 | 49.3 | 219.1 | 216.2 | 216.2 | YES
14 | ** OPTIMAL ** | 6 | 5 | 7 | 5 | 41.1 | 5.06 | 50 | 79 | 42.5 | 66.2 | 48.3 | 219.1 | 216.2 | 216.2 | YES
15 | OK | 5 | 3 | 3 | 4 | 84.6 | 5.06 | 50 | 79 | 42.5 | 66.2 | 48.3 | 219.1 | 216.2 | 216.2 | YES
16 | OK | 3 | 4 | 4 | 4 | 132.6 | 5.06 | 50 | 79 | 42.5 | 66.2 | 48.3 | 219.1 | 216.2 | 216.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-017654
TR_B (available) | 58-015644
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 79
TR_B Baseline Loading% | 42.5
Total Scenarios Evaluated | 17
Feasible Scenarios | 16
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 5
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 5
Tie Line Distance (m) | 41.1
Load Transferred (kW) | 5.06
TR_A Loading After (%) | 66.2
TR_B Loading After (%) | 48.3
Minimum Voltage (V) | 216.2