## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 15 | 31 | 53 | 2.4 | 22.74 | 95 | 79.4 | 45.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 16 | 47 | 36 | 38 | 106.9 | 11.29 | 50 | 79.4 | 45.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 15 | 32 | 31 | 53 | 2.4 | 22.74 | 95 | 79.4 | 45.2 | 25.9 | 62.2 | 227.2 | 214.2 | 214.2 | YES
2 | OK | 47 | 46 | 36 | 38 | 106.9 | 11.01 | 50 | 79.4 | 45.2 | 54 | 50.6 | 216.1 | 212 | 212 | YES
3 | OK | 32 | 14 | 53 | 53 | 14.8 | 1.96 | 50 | 79.4 | 45.2 | 74.8 | 46.7 | 215.5 | 217.7 | 215.5 | YES
4 | OK | 32 | 45 | 31 | 53 | 2.4 | 20.78 | 95 | 79.4 | 45.2 | 30.4 | 60.7 | 226.3 | 216.7 | 216.7 | YES
5 | OK | 46 | 24 | 36 | 38 | 106.9 | 8.95 | 50 | 79.4 | 45.2 | 58.7 | 50.6 | 216.2 | 212 | 212 | YES
6 | OK | 14 | 13 | 53 | 53 | 14.8 | 1.38 | 50 | 79.4 | 45.2 | 76.2 | 46.2 | 215.1 | 217.8 | 215.1 | YES
7 | OK | 45 | 23 | 31 | 53 | 2.4 | 20.78 | 95 | 79.4 | 45.2 | 30.4 | 60.7 | 226.3 | 216.7 | 216.7 | YES
8 | OK | 24 | 25 | 36 | 38 | 106.9 | 8.95 | 50 | 79.4 | 45.2 | 58.7 | 50.6 | 216.2 | 212 | 212 | YES
9 | OK | 13 | 49 | 53 | 53 | 14.8 | 1.38 | 50 | 79.4 | 45.2 | 76.2 | 46.2 | 215.1 | 217.8 | 215.1 | YES
10 | OK | 23 | 22 | 31 | 53 | 2.4 | 20.78 | 95 | 79.4 | 45.2 | 30.4 | 60.7 | 226.3 | 216.7 | 216.7 | YES
11 | OK | 25 | 17 | 36 | 38 | 106.9 | 8.48 | 50 | 79.4 | 45.2 | 59.8 | 50.6 | 216.2 | 212 | 212 | YES
12 | OK | 49 | 50 | 53 | 53 | 14.8 | 0.75 | 50 | 79.4 | 45.2 | 77.6 | 45.8 | 214.7 | 217.9 | 214.7 | YES
13 | OK | 22 | 21 | 31 | 53 | 2.4 | 20.35 | 95 | 79.4 | 45.2 | 31.4 | 60.3 | 226.2 | 216.8 | 216.8 | YES
14 | OK | 17 | 18 | 36 | 38 | 106.9 | 2.58 | 50 | 79.4 | 45.2 | 73.4 | 47.2 | 214.7 | 217.5 | 214.7 | YES
15 | OK | 17 | 19 | 29 | 35 | 136.1 | 5.9 | 50 | 79.4 | 45.2 | 65.7 | 49.8 | 215.8 | 214.1 | 214.1 | YES
16 | OK | 50 | 54 | 53 | 53 | 14.8 | 0.75 | 50 | 79.4 | 45.2 | 77.6 | 45.8 | 214.7 | 217.9 | 214.7 | YES
17 | OK | 21 | 7 | 31 | 53 | 2.4 | 19.49 | 95 | 79.4 | 45.2 | 33.4 | 59.7 | 226.1 | 216.8 | 216.8 | YES
18 | OK | 18 | 57 | 36 | 38 | 106.9 | 1.97 | 50 | 79.4 | 45.2 | 74.8 | 46.7 | 214.6 | 217.8 | 214.6 | YES
19 | OK | 19 | 26 | 29 | 35 | 136.1 | 4.14 | 50 | 79.4 | 45.2 | 69.8 | 48.4 | 215.2 | 216.5 | 215.2 | YES
20 | OK | 54 | 52 | 53 | 53 | 14.8 | 0.41 | 50 | 79.4 | 45.2 | 78.4 | 45.5 | 214.5 | 217.9 | 214.5 | YES
21 | OK | 7 | 5 | 31 | 53 | 2.4 | 18.7 | 95 | 79.4 | 45.2 | 35.2 | 59.1 | 226.1 | 216.8 | 216.8 | YES
22 | OK | 57 | 42 | 36 | 38 | 106.9 | 1.35 | 50 | 79.4 | 45.2 | 76.2 | 46.3 | 214.6 | 217.6 | 214.6 | YES
23 | OK | 26 | 27 | 29 | 35 | 136.1 | 2.33 | 50 | 79.4 | 45.2 | 74 | 47 | 214.8 | 217.1 | 214.8 | YES
24 | OK | 5 | 6 | 31 | 53 | 2.4 | 14.57 | 95 | 79.4 | 45.2 | 44.9 | 56 | 219.5 | 217.4 | 217.4 | YES
25 | OK | 5 | 20 | 58 | 8 | 65.3 | 4.13 | 50 | 79.4 | 45.2 | 69.4 | 48.3 | 219.8 | 217.5 | 217.5 | YES
26 | OK | 42 | 43 | 36 | 38 | 106.9 | 1.35 | 50 | 79.4 | 45.2 | 76.2 | 46.3 | 214.6 | 217.6 | 214.6 | YES
27 | OK | 27 | 28 | 29 | 35 | 136.1 | 1.94 | 50 | 79.4 | 45.2 | 74.9 | 46.7 | 214.6 | 217.4 | 214.6 | YES
28 | OK | 6 | 10 | 31 | 53 | 2.4 | 14.29 | 95 | 79.4 | 45.2 | 45.5 | 55.8 | 219.6 | 217.4 | 217.4 | YES
29 | OK | 20 | 44 | 58 | 8 | 65.3 | 4.13 | 50 | 79.4 | 45.2 | 69.4 | 48.3 | 219.8 | 217.5 | 217.5 | YES
30 | OK | 43 | 33 | 36 | 38 | 106.9 | 1.35 | 50 | 79.4 | 45.2 | 76.2 | 46.3 | 214.6 | 217.6 | 214.6 | YES
| NG | 28 | 29 | 29 | 35 | 136.1 | 0.59 | 50 | 79.4 | 45.2 | 78 | 783.5 | 214.4 | 5.5 | 5.5 | NO
31 | OK | 10 | 11 | 31 | 53 | 2.4 | 0.23 | 95 | 79.4 | 45.2 | 78.8 | 45.4 | 214.6 | 217.9 | 214.6 | YES
32 | OK | 10 | 12 | 12 | 53 | 75 | 7.02 | 50 | 79.4 | 45.2 | 62.6 | 50.4 | 217.2 | 217.7 | 217.2 | YES
33 | OK | 10 | 30 | 8 | 9 | 71.2 | 6.17 | 50 | 79.4 | 45.2 | 62.6 | 49.8 | 216.4 | 217.7 | 216.4 | YES
34 | OK | 44 | 58 | 58 | 8 | 65.3 | 3.85 | 50 | 79.4 | 45.2 | 70 | 48.1 | 219.8 | 217.5 | 217.5 | YES
35 | OK | 33 | 34 | 36 | 38 | 106.9 | 0.66 | 50 | 79.4 | 45.2 | 77.8 | 45.7 | 214.6 | 217.4 | 214.6 | YES
36 | OK | 12 | 40 | 40 | 53 | 93 | 5.43 | 50 | 79.4 | 45.2 | 66.3 | 49.2 | 216.2 | 217.8 | 216.2 | YES
37 | OK | 30 | 41 | 8 | 9 | 71.2 | 5.09 | 50 | 79.4 | 45.2 | 67.2 | 49 | 216.2 | 217.8 | 216.2 | YES
38 | ** OPTIMAL ** | 58 | 48 | 48 | 8 | 68.1 | 3.71 | 50 | 79.4 | 45.2 | 70.4 | 48 | 219.9 | 217.5 | 217.5 | YES
39 | OK | 34 | 35 | 36 | 38 | 106.9 | 0.57 | 50 | 79.4 | 45.2 | 78 | 45.7 | 214.6 | 217.4 | 214.6 | YES
40 | OK | 40 | 39 | 39 | 53 | 124.6 | 3.58 | 50 | 79.4 | 45.2 | 70.7 | 47.9 | 215.3 | 217.8 | 215.3 | YES
41 | OK | 41 | 9 | 8 | 9 | 71.2 | 3.52 | 50 | 79.4 | 45.2 | 70.9 | 47.8 | 216.5 | 217.8 | 216.5 | YES
42 | OK | 48 | 1 | 0 | 8 | 103 | 0.68 | 50 | 79.4 | 45.2 | 77.7 | 45.3 | 214.4 | 217.9 | 214.4 | YES
43 | OK | 9 | 8 | 8 | 9 | 71.2 | 2 | 50 | 79.4 | 45.2 | 74.6 | 45.2 | 213.9 | 218 | 213.9 | YES
44 | OK | 1 | 0 | 0 | 8 | 103 | 0.09 | 50 | 79.4 | 45.2 | 79.1 | 45.3 | 214.5 | 217.9 | 214.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-017987
TR_B (available) | 42-005139
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 79.4
TR_B Baseline Loading% | 45.2
Total Scenarios Evaluated | 47
Feasible Scenarios | 44
--- Optimal Solution ---
Switch Parent Node | 58
Switch Child Node | 48
Tie Node (TR_A side) | 48
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 68.1
Load Transferred (kW) | 3.71
TR_A Loading After (%) | 70.4
TR_B Loading After (%) | 48
Minimum Voltage (V) | 217.5