## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 32 | 45 | 2 | 11 | 2 | 20.78 | 50 | 79.4 | 10.7 | 30.4 | 71.8 | 226.3 | 192.2 | 192.2 | NO
| NG | 45 | 23 | 2 | 11 | 2 | 20.78 | 50 | 79.4 | 10.7 | 30.4 | 71.8 | 226.3 | 192.2 | 192.2 | NO
| NG | 23 | 22 | 2 | 11 | 2 | 20.78 | 50 | 79.4 | 10.7 | 30.4 | 71.8 | 226.3 | 192.2 | 192.2 | NO
| NG | 22 | 21 | 2 | 11 | 2 | 20.35 | 50 | 79.4 | 10.7 | 31.4 | 70.9 | 226.2 | 193.3 | 193.3 | NO
| NG | 21 | 7 | 2 | 11 | 2 | 19.49 | 50 | 79.4 | 10.7 | 33.4 | 69.8 | 226.1 | 194.7 | 194.7 | NO
| NG | 7 | 5 | 2 | 11 | 2 | 18.7 | 50 | 79.4 | 10.7 | 35.2 | 66.7 | 226.1 | 194.3 | 194.3 | NO
1 | OK | 5 | 20 | 2 | 11 | 2 | 4.13 | 50 | 79.4 | 10.7 | 69.4 | 27 | 219.8 | 217.6 | 217.6 | YES
2 | OK | 20 | 44 | 2 | 11 | 2 | 4.13 | 50 | 79.4 | 10.7 | 69.4 | 27 | 219.8 | 217.6 | 217.6 | YES
3 | OK | 44 | 58 | 2 | 11 | 2 | 3.85 | 50 | 79.4 | 10.7 | 70 | 25.9 | 219.8 | 218.8 | 218.8 | YES
4 | ** OPTIMAL ** | 58 | 48 | 2 | 11 | 2 | 3.71 | 50 | 79.4 | 10.7 | 70.4 | 25.3 | 219.9 | 219.3 | 219.3 | YES
5 | OK | 48 | 1 | 2 | 11 | 2 | 0.68 | 50 | 79.4 | 10.7 | 77.7 | 13.3 | 214.4 | 225.4 | 214.4 | YES
6 | OK | 1 | 59 | 2 | 11 | 2 | 0.59 | 50 | 79.4 | 10.7 | 78 | 13 | 214.2 | 225.3 | 214.2 | YES
7 | OK | 59 | 4 | 2 | 11 | 2 | 0.45 | 50 | 79.4 | 10.7 | 78.3 | 12.4 | 214.2 | 225.7 | 214.2 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 58-017987
TR_B (available) | 52-007703
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79.4
TR_B Baseline Loading% | 10.7
Total Scenarios Evaluated | 13
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 58
Switch Child Node | 48
Tie Node (TR_A side) | 2
Tie Node (TR_B side) | 11
Tie Line Distance (m) | 2
Load Transferred (kW) | 3.71
TR_A Loading After (%) | 70.4
TR_B Loading After (%) | 25.3
Minimum Voltage (V) | 219.3