## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 16 | 47 | 56 | 13 | 80.7 | 11.29 | 50 | 79.4 | 6.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 47 | 46 | 56 | 13 | 80.7 | 11.01 | 50 | 79.4 | 6.1 | 54 | 38 | 216.1 | 213.9 | 213.9 | YES
2 | OK | 46 | 24 | 56 | 13 | 80.7 | 8.95 | 50 | 79.4 | 6.1 | 58.7 | 29.4 | 216.2 | 213.1 | 213.1 | YES
3 | OK | 24 | 25 | 56 | 13 | 80.7 | 8.95 | 50 | 79.4 | 6.1 | 58.7 | 29.4 | 216.2 | 213.1 | 213.1 | YES
4 | OK | 25 | 17 | 56 | 13 | 80.7 | 8.48 | 50 | 79.4 | 6.1 | 59.8 | 27.6 | 216.2 | 212.9 | 212.9 | YES
5 | ** OPTIMAL ** | 17 | 19 | 56 | 13 | 80.7 | 5.9 | 50 | 79.4 | 6.1 | 65.7 | 24.2 | 215.8 | 217.4 | 215.8 | YES
6 | OK | 19 | 26 | 56 | 13 | 80.7 | 4.14 | 50 | 79.4 | 6.1 | 69.8 | 17.1 | 215.2 | 222.4 | 215.2 | YES
7 | OK | 26 | 27 | 56 | 13 | 80.7 | 2.33 | 50 | 79.4 | 6.1 | 74 | 13.3 | 214.8 | 226.1 | 214.8 | YES
8 | OK | 27 | 28 | 56 | 13 | 80.7 | 1.94 | 50 | 79.4 | 6.1 | 74.9 | 12.2 | 214.6 | 227.1 | 214.6 | YES
| NG | 28 | 29 | 56 | 13 | 80.7 | 0.59 | 50 | 79.4 | 6.1 | [5 empty] | NO | TR_B sim: not converged

## Summary
Parameter | Value
TR_A (overloaded) | 58-017987
TR_B (available) | 63-034945
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79.4
TR_B Baseline Loading% | 6.1
Total Scenarios Evaluated | 10
Feasible Scenarios | 8
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 19
Tie Node (TR_A side) | 56
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 80.7
Load Transferred (kW) | 5.9
TR_A Loading After (%) | 65.7
TR_B Loading After (%) | 24.2
Minimum Voltage (V) | 215.8