## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 54 | 5 | 78 | 36 | 141 | 9.58 | 50 | 57.1 | 23.7 | 33.4 | 52.4 | 221.4 | 183.8 | 183.8 | NO
1 | OK | 5 | 18 | 78 | 36 | 141 | 1.13 | 50 | 57.1 | 23.7 | 52.8 | 28.3 | 217.6 | 216.8 | 216.8 | YES
2 | OK | 18 | 53 | 78 | 36 | 141 | 1.13 | 50 | 57.1 | 23.7 | 52.8 | 28.3 | 217.6 | 216.8 | 216.8 | YES
3 | OK | 53 | 60 | 78 | 36 | 141 | 0.27 | 50 | 57.1 | 23.7 | 56.1 | 24.8 | 216.9 | 221.2 | 216.9 | YES
4 | OK | 53 | 77 | 73 | 28 | 204.8 | 0.86 | 50 | 57.1 | 23.7 | 53.8 | 27.2 | 217.4 | 219.2 | 217.4 | YES
5 | OK | 60 | 61 | 78 | 36 | 141 | 0.25 | 50 | 57.1 | 23.7 | 56.1 | 24.7 | 216.9 | 221.3 | 216.9 | YES
6 | ** OPTIMAL ** | 77 | 72 | 73 | 28 | 204.8 | 0.86 | 50 | 57.1 | 23.7 | 53.8 | 27.2 | 217.4 | 219.2 | 217.4 | YES
7 | OK | 61 | 48 | 78 | 36 | 141 | 0.25 | 50 | 57.1 | 23.7 | 56.2 | 24.7 | 216.9 | 221.3 | 216.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 59-002939
TR_B (available) | 50-006353
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 57.1
TR_B Baseline Loading% | 23.7
Total Scenarios Evaluated | 8
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 77
Switch Child Node | 72
Tie Node (TR_A side) | 73
Tie Node (TR_B side) | 28
Tie Line Distance (m) | 204.8
Load Transferred (kW) | 0.86
TR_A Loading After (%) | 53.8
TR_B Loading After (%) | 27.2
Minimum Voltage (V) | 217.4