## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 54 | 2 | 4 | 7 | 119.7 | 0.38 | 50 | 57.1 | 12.5 | 54.6 | 12.5 | 216.8 | 227.2 | 216.8 | YES
2 | OK | 54 | 40 | 13 | 7 | 3 | 13.03 | 50 | 57.1 | 12.5 | 26.3 | 43.8 | 223.3 | 216.6 | 216.6 | YES
3 | OK | 2 | 4 | 4 | 7 | 119.7 | 0.38 | 50 | 57.1 | 12.5 | 54.6 | 12.5 | 216.8 | 227.2 | 216.8 | YES
4 | OK | 40 | 39 | 39 | 7 | 88.1 | 3.51 | 50 | 57.1 | 12.5 | 56.1 | 13.7 | 215.9 | 226.9 | 215.9 | YES
| NG | 40 | 8 | 6 | 7 | 10.5 | 2.13 | 50 | 57.1 | 12.5 | 49 | 20.7 | 47.4 | 225.4 | 47.4 | NO
5 | OK | 40 | 23 | 91 | 30 | 32.9 | 7.39 | 50 | 57.1 | 12.5 | 35.6 | 34.4 | 221.5 | 217.8 | 217.8 | YES
6 | OK | 39 | 38 | 38 | 7 | 94.3 | 3.2 | 50 | 57.1 | 12.5 | 57.3 | 12.5 | 215.7 | 227.2 | 215.7 | YES
| NG | 8 | 7 | 6 | 7 | 10.5 | 2.09 | 50 | 57.1 | 12.5 | 49.1 | 20.5 | 47.4 | 225.4 | 47.4 | NO
7 | OK | 23 | 24 | 36 | 7 | 148.1 | 0.67 | 50 | 57.1 | 12.5 | 57.3 | 12.5 | 215.7 | 227.2 | 215.7 | YES
8 | OK | 23 | 21 | 91 | 30 | 32.9 | 6.72 | 50 | 57.1 | 12.5 | 35.6 | 34.4 | 221.5 | 217.8 | 217.8 | YES
9 | OK | 38 | 26 | 26 | 7 | 115.3 | 2.99 | 50 | 57.1 | 12.5 | 57.3 | 12.5 | 215.7 | 227.2 | 215.7 | YES
| NG | 7 | 6 | 6 | 7 | 10.5 | 1.93 | 50 | 57.1 | 12.5 | 49.7 | 19.9 | 47.4 | 225.6 | 47.4 | NO
10 | OK | 24 | 36 | 36 | 7 | 148.1 | 0.23 | 50 | 57.1 | 12.5 | 57.3 | 12.5 | 215.7 | 227.2 | 215.7 | YES
| NG | 21 | 16 | 91 | 30 | 32.9 | 2.88 | 50 | 57.1 | 12.5 | [5 empty] | NO | TR_A sim: loading inf% (degenerate)
| NG | 21 | 58 | 15 | 7 | 56.2 | 0.81 | 50 | 57.1 | 12.5 | [5 empty] | NO | TR_B sim: not converged
11 | OK | 26 | 25 | 25 | 7 | 124 | 1.86 | 50 | 57.1 | 12.5 | 57.3 | 12.5 | 215.7 | 227.2 | 215.7 | YES
| NG | 16 | 17 | 91 | 30 | 32.9 | 2.62 | 50 | 57.1 | 12.5 | [5 empty] | NO | TR_A sim: not converged
| NG | 58 | 57 | 15 | 7 | 56.2 | 0.81 | 50 | 57.1 | 12.5 | 54.4 |  | 217.8 | 2281055454697502 | 217.8 | NO
12 | OK | 25 | 0 | 0 | 7 | 126.1 | 1.78 | 50 | 57.1 | 12.5 | 57.1 | 12.5 | 216.7 | 227.2 | 216.7 | YES
13 | ** OPTIMAL ** | 17 | 10 | 91 | 30 | 32.9 | 2.62 | 50 | 57.1 | 12.5 | 51 | 18.6 | 218.5 | 225.7 | 218.5 | YES
14 | OK | 57 | 15 | 15 | 7 | 56.2 | 0.81 | 50 | 57.1 | 12.5 | 54.4 | 15.2 | 217.5 | 226.6 | 217.5 | YES
15 | OK | 0 | 1 | 1 | 7 | 145 | 1.56 | 50 | 57.1 | 12.5 | 57.1 | 12.5 | 216.7 | 227.2 | 216.7 | YES
16 | OK | 10 | 9 | 91 | 30 | 32.9 | 1.31 | 50 | 57.1 | 12.5 | 53.9 | 15.7 | 217.9 | 226.4 | 217.9 | YES
17 | OK | 15 | 11 | 11 | 7 | 60.8 | 0.81 | 50 | 57.1 | 12.5 | 54.4 | 15.2 | 217.5 | 226.6 | 217.5 | YES
| NG | 1 | 37 | 37 | 7 | 147.5 | 1.13 | 50 | 57.1 | 12.5 | [5 empty] | NO | TR_B sim: not converged
18 | OK | 9 | 90 | 91 | 30 | 32.9 | 0.66 | 50 | 57.1 | 12.5 | 55.7 | 12.5 | 217.3 | 227.2 | 217.3 | YES
| NG | 11 | 12 | 12 | 7 | 85 | 0.81 | 50 | 57.1 | 12.5 | 54.4 | 15.2 | 46.8 | 226.6 | 46.8 | NO
19 | OK | 90 | 67 | 91 | 30 | 32.9 | 0.3 | 50 | 57.1 | 12.5 | 57.1 | 12.5 | 216.6 | 227.2 | 216.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 59-002939
TR_B (available) | 55-010117
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 57.1
TR_B Baseline Loading% | 12.5
Total Scenarios Evaluated | 28
Feasible Scenarios | 19
--- Optimal Solution ---
Switch Parent Node | 17
Switch Child Node | 10
Tie Node (TR_A side) | 91
Tie Node (TR_B side) | 30
Tie Line Distance (m) | 32.9
Load Transferred (kW) | 2.62
TR_A Loading After (%) | 51
TR_B Loading After (%) | 18.6
Minimum Voltage (V) | 218.5