## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 9 | 16 | 16 | 25 | 102.7 | 3.92 | 50 | 81 | 25.6 | 71.9 | 32.4 | 59.6 | 218.7 | 59.6 | NO
| NG | 9 | 5 | 5 | 25 | 41.1 | 1.87 | 50 | 81 | 25.6 | 46.4 | 29.5 | 59 | 220.1 | 59 | NO
| NG | 10 | 15 | 18 | 25 | 93.1 | 11.99 | 50 | 81 | 25.6 | 52.9 | 62.4 | 60.9 | 198.9 | 60.9 | NO
| NG | 10 | 8 | 8 | 25 | 104.6 | 14.96 | 50 | 81 | 25.6 | 45.9 | 52.4 | 221.7 | 204.2 | 204.2 | NO
| NG | 10 | 6 | 6 | 25 | 67 | 1.25 | 50 | 81 | 25.6 | 50.5 | 25.9 | 58.9 | 221.7 | 58.9 | NO
| NG | 16 | 21 | 21 | 25 | 104.9 | 2.41 | 50 | 81 | 25.6 | 75.4 | 29.3 | 59.5 | 220.1 | 59.5 | NO
| NG | 15 | 20 | 20 | 25 | 131.2 | 8.91 | 50 | 81 | 25.6 | 57 | 56.8 | 60.8 | 202.6 | 60.8 | NO
| NG | 8 | 12 | 14 | 25 | 137.7 | 14.28 | 50 | 81 | 25.6 | 47.5 | 52.4 | 221.7 | 203.6 | 203.6 | NO
| NG | 8 | 13 | 13 | 25 | 121.3 | 0.68 | 50 | 81 | 25.6 | 61.1 | 25.6 | 59 | 221.8 | 59 | NO
| NG | 21 | 24 | 24 | 25 | 143.8 | 2.41 | 50 | 81 | 25.6 | 75.4 | 25.6 | 59.5 | 221.8 | 59.5 | NO
| NG | 20 | 32 | 32 | 25 | 167.7 | 8.06 | 50 | 81 | 25.6 | 62 | 56.9 | 60.7 | 202.1 | 60.7 | NO
| NG | 12 | 14 | 14 | 25 | 137.7 | 1.29 | 50 | 81 | 25.6 | 60.5 | 29.2 | 59.2 | 220.2 | 59.2 | NO
| NG | 12 | 19 | 19 | 25 | 168.4 | 1.58 | 50 | 81 | 25.6 | 69.6 | 26.7 | 59.3 | 221.3 | 59.3 | NO
1 | ** OPTIMAL ** | 12 | 26 | 28 | 14 | 158.1 | 8.25 | 50 | 81 | 25.6 | 61.5 | 45.7 | 220.9 | 211.6 | 211.6 | YES
| NG | 32 | 33 | 33 | 25 | 204.8 | 0.66 | 50 | 81 | 25.6 | 79.4 | 25.6 | 59.3 | 221.8 | 59.3 | NO
| NG | 19 | 25 | 25 | 9 | 175.8 | 1.3 | 50 | 81 | 25.6 | 70.2 | 26.7 | 59.2 | 221.6 | 59.2 | NO
| NG | 26 | 29 | 28 | 14 | 158.1 | 6.15 | 50 | 81 | 25.6 | 66.4 | 41.4 | 60.5 | 214.1 | 60.5 | NO
| NG | 29 | 30 | 28 | 14 | 158.1 | 4.44 | 50 | 81 | 25.6 | 70.4 | 36.1 | 60.1 | 217.6 | 60.1 | NO
| NG | 30 | 31 | 28 | 14 | 158.1 | 3.56 | 50 | 81 | 25.6 | 72.5 | 32.5 | 59.8 | 219.6 | 59.8 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 59-003247
TR_B (available) | 68-018197
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81
TR_B Baseline Loading% | 25.6
Total Scenarios Evaluated | 19
Feasible Scenarios | 1
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 26
Tie Node (TR_A side) | 28
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 158.1
Load Transferred (kW) | 8.25
TR_A Loading After (%) | 61.5
TR_B Loading After (%) | 45.7
Minimum Voltage (V) | 211.6