## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 52 | 16 | 20 | 4 | 24.8 | 25.04 | 50 | 63.7 | 21.3 | 50.7 | 79.7 | 6 | 219.5 | 6 | NO
1 | OK | 13 | 14 | 18 | 2 | 87.5 | 2.98 | 50 | 63.7 | 21.3 | 60.2 | 28.1 | 220.2 | 227.6 | 220.2 | YES
2 | OK | 13 | 11 | 48 | 2 | 11.9 | 26.94 | 50 | 63.7 | 21.3 | 32.2 | 41.4 | 226.5 | 222.4 | 222.4 | YES
3 | OK | 16 | 17 | 20 | 4 | 24.8 | 24.91 | 50 | 63.7 | 21.3 | 35 | 74.6 | 222.2 | 219.1 | 219.1 | YES
4 | OK | 14 | 18 | 18 | 2 | 87.5 | 1.24 | 50 | 63.7 | 21.3 | 62.2 | 24.1 | 220.2 | 228.5 | 220.2 | YES
| NG | 11 | 12 | 48 | 2 | 11.9 | 26.9 | 50 | 63.7 | 21.3 | 32.3 |  | 226.5 | 2281055454697502 | 226.5 | NO
5 | OK | 11 | 45 | 45 | 2 | 137.9 | 0.03 | 50 | 63.7 | 21.3 | 63.6 | 21.3 | 220.2 | 228.8 | 220.2 | YES
6 | OK | 17 | 19 | 20 | 4 | 24.8 | 22.52 | 50 | 63.7 | 21.3 | 37.7 | 73.7 | 222.2 | 219.1 | 219.1 | YES
| NG | 17 | 44 | 44 | 7 | 140.8 | 2.01 | 50 | 63.7 | 21.3 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 21.3% (degenerate)
7 | OK | 12 | 46 | 46 | 2 | 132.2 | 0.06 | 50 | 63.7 | 21.3 | 63.6 | 21.3 | 220.7 | 228.8 | 220.7 | YES
8 | OK | 12 | 4 | 48 | 2 | 11.9 | 26.84 | 50 | 63.7 | 21.3 | 32.3 | 41.4 | 226.5 | 222.4 | 222.4 | YES
9 | OK | 19 | 34 | 20 | 4 | 24.8 | 14.17 | 50 | 63.7 | 21.3 | 47.3 | 54 | 221.5 | 223.1 | 221.5 | YES
10 | OK | 4 | 5 | 48 | 2 | 11.9 | 26.84 | 50 | 63.7 | 21.3 | 32.3 | 41.4 | 226.5 | 222.4 | 222.4 | YES
11 | OK | 34 | 35 | 57 | 4 | 79.1 | 6.03 | 50 | 63.7 | 21.3 | 56.7 | 28.3 | 220.9 | 225 | 220.9 | YES
12 | OK | 34 | 32 | 20 | 4 | 24.8 | 8.14 | 50 | 63.7 | 21.3 | 54.2 | 40 | 220.9 | 226.5 | 220.9 | YES
| NG | 5 | 29 | 48 | 2 | 11.9 | 26.84 | 50 | 63.7 | 21.3 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 21.3% (degenerate)
13 | OK | 35 | 36 | 57 | 4 | 79.1 | 6.03 | 50 | 63.7 | 21.3 | 56.7 | 22.6 | 220.9 | 228.3 | 220.9 | YES
14 | OK | 32 | 33 | 20 | 4 | 24.8 | 6.27 | 50 | 63.7 | 21.3 | 56.4 | 35.7 | 220.9 | 226.4 | 220.9 | YES
15 | OK | 29 | 8 | 48 | 2 | 11.9 | 26.45 | 50 | 63.7 | 21.3 | 32.8 | 41.4 | 226.5 | 222.4 | 222.4 | YES
16 | OK | 36 | 37 | 57 | 4 | 79.1 | 3.57 | 50 | 63.7 | 21.3 | 59.5 | 22.6 | 220.3 | 228.3 | 220.3 | YES
17 | OK | 33 | 43 | 20 | 4 | 24.8 | 6.27 | 50 | 63.7 | 21.3 | 56.4 | 35.7 | 220.9 | 226.4 | 220.9 | YES
18 | OK | 8 | 7 | 48 | 2 | 11.9 | 20.32 | 50 | 63.7 | 21.3 | 39.8 | 33 | 226.2 | 225 | 225 | YES
19 | OK | 8 | 9 | 9 | 2 | 73.2 | 3.98 | 50 | 63.7 | 21.3 | 59 | 24.5 | 220.4 | 228.5 | 220.4 | YES
20 | OK | 37 | 41 | 57 | 4 | 79.1 | 3.23 | 50 | 63.7 | 21.3 | 59.9 | 22.6 | 220.3 | 228.3 | 220.3 | YES
21 | OK | 43 | 27 | 20 | 4 | 24.8 | 6.27 | 50 | 63.7 | 21.3 | 56.4 | 35.7 | 220.9 | 226.4 | 220.9 | YES
22 | OK | 7 | 6 | 6 | 8 | 43.4 | 15.42 | 50 | 63.7 | 21.3 | 45.5 | 56.7 | 225.6 | 224.9 | 224.9 | YES
23 | OK | 7 | 47 | 48 | 2 | 11.9 | 0.23 | 50 | 63.7 | 21.3 | 63.4 | 21.8 | 220.2 | 228.8 | 220.2 | YES
24 | OK | 9 | 10 | 10 | 2 | 75.1 | 2.2 | 50 | 63.7 | 21.3 | 61.1 | 21.3 | 220.1 | 228.8 | 220.1 | YES
25 | OK | 41 | 42 | 57 | 4 | 79.1 | 3.23 | 50 | 63.7 | 21.3 | 59.9 | 22.6 | 220.3 | 228.3 | 220.3 | YES
26 | OK | 27 | 28 | 20 | 4 | 24.8 | 4.42 | 50 | 63.7 | 21.3 | 58.5 | 31.4 | 220.5 | 227.7 | 220.5 | YES
27 | ** OPTIMAL ** | 6 | 26 | 26 | 8 | 51.8 | 11.52 | 50 | 63.7 | 21.3 | 50 | 47.8 | 225.4 | 225.6 | 225.4 | YES
28 | OK | 47 | 48 | 48 | 2 | 11.9 | 0.23 | 50 | 63.7 | 21.3 | 63.4 | 21.3 | 220.2 | 228.8 | 220.2 | YES
29 | OK | 42 | 38 | 57 | 4 | 79.1 | 2.26 | 50 | 63.7 | 21.3 | 60.6 | 22.6 | 220.3 | 228.3 | 220.3 | YES
30 | OK | 28 | 20 | 20 | 4 | 24.8 | 1.17 | 50 | 63.7 | 21.3 | 62.3 | 24 | 220.2 | 228.8 | 220.2 | YES
| NG | 26 | 1 | 1 | 8 | 53.5 | 9.06 | 50 | 63.7 | 21.3 | 453.1 | 42.1 | 35 | 227.1 | 35 | NO
31 | OK | 38 | 39 | 57 | 4 | 79.1 | 2.26 | 50 | 63.7 | 21.3 | 61 | 22.6 | 220.3 | 228.3 | 220.3 | YES
32 | OK | 1 | 0 | 55 | 1 | 62.8 | 7.65 | 50 | 63.7 | 21.3 | 54.6 | 38.9 | 222.8 | 227 | 222.8 | YES
33 | OK | 39 | 40 | 57 | 4 | 79.1 | 0.5 | 50 | 63.7 | 21.3 | 63.1 | 21.6 | 220.2 | 228.7 | 220.2 | YES
34 | OK | 0 | 22 | 55 | 1 | 62.8 | 5.48 | 50 | 63.7 | 21.3 | 57.1 | 33.9 | 223 | 227.3 | 223 | YES
35 | OK | 22 | 23 | 55 | 1 | 62.8 | 2.59 | 50 | 63.7 | 21.3 | 60.5 | 27.2 | 222 | 228.1 | 222 | YES
36 | OK | 22 | 51 | 51 | 1 | 75 | 2.78 | 50 | 63.7 | 21.3 | 60.3 | 27.7 | 221.2 | 228.1 | 221.2 | YES
37 | OK | 23 | 49 | 55 | 1 | 62.8 | 1.52 | 50 | 63.7 | 21.3 | 61.8 | 24.8 | 222 | 228.1 | 222 | YES
38 | OK | 51 | 24 | 24 | 1 | 77.9 | 1.72 | 50 | 63.7 | 21.3 | 61.6 | 25.2 | 219.7 | 228.1 | 219.7 | YES
39 | OK | 49 | 50 | 55 | 1 | 62.8 | 0.18 | 50 | 63.7 | 21.3 | 63.4 | 21.7 | 220.1 | 228.8 | 220.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 59-020571
TR_B (available) | 37-010398
TR_A Rated kVA | 100
TR_B Rated kVA | 50
TR_A Baseline Loading% | 63.7
TR_B Baseline Loading% | 21.3
Total Scenarios Evaluated | 44
Feasible Scenarios | 39
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 26
Tie Node (TR_A side) | 26
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 51.8
Load Transferred (kW) | 11.52
TR_A Loading After (%) | 50
TR_B Loading After (%) | 47.8
Minimum Voltage (V) | 225.4