## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 52 | 13 | 4 | 75 | 18.6 | 29.92 | 50 | 63.7 | 27.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 52 | 16 | 16 | 76 | 41.7 | 25.04 | 50 | 63.7 | 27.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 13 | 14 | 14 | 75 | 52.9 | 2.98 | 50 | 63.7 | 27.8 | 60.2 | 29.1 | 220.2 | 213.7 | 213.7 | YES
| NG | 13 | 11 | 4 | 75 | 18.6 | 26.94 | 50 | 63.7 | 27.8 | 32.2 | 41 | 226.5 | 209.1 | 209.1 | NO
2 | ** OPTIMAL ** | 16 | 17 | 31 | 55 | 44.8 | 24.91 | 50 | 63.7 | 27.8 | 35 | 31.4 | 222.2 | 213.7 | 213.7 | YES
3 | OK | 14 | 18 | 18 | 75 | 60 | 1.24 | 50 | 63.7 | 27.8 | 62.2 | 28.3 | 220.2 | 213.7 | 213.7 | YES
| NG | 11 | 12 | 4 | 75 | 18.6 | 26.9 | 50 | 63.7 | 27.8 | 32.3 |  | 226.5 | 593942.1 | 226.5 | NO
4 | OK | 11 | 45 | 45 | 76 | 29.6 | 0.03 | 50 | 63.7 | 27.8 | 63.6 | 27.8 | 220.2 | 213.7 | 213.7 | YES
5 | OK | 17 | 19 | 31 | 55 | 44.8 | 22.52 | 50 | 63.7 | 27.8 | 37.7 | 31.2 | 222.2 | 213.7 | 213.7 | YES
| NG | 17 | 44 | 44 | 76 | 50.2 | 2.01 | 50 | 63.7 | 27.8 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 27.8% (degenerate)
6 | OK | 12 | 46 | 46 | 75 | 21.4 | 0.06 | 50 | 63.7 | 27.8 | 63.6 | 27.8 | 220.7 | 213.7 | 213.7 | YES
| NG | 12 | 4 | 4 | 75 | 18.6 | 26.84 | 50 | 63.7 | 27.8 | 32.3 | 40.9 | 226.5 | 209.1 | 209.1 | NO
7 | OK | 19 | 2 | 2 | 76 | 101.2 | 3.87 | 50 | 63.7 | 27.8 | 59.2 | 29.6 | 220.7 | 213.5 | 213.5 | YES
8 | OK | 19 | 34 | 34 | 76 | 91.7 | 14.17 | 50 | 63.7 | 27.8 | 47.3 | 34.5 | 221.5 | 213.2 | 213.2 | YES
9 | OK | 19 | 21 | 31 | 55 | 44.8 | 4.48 | 50 | 63.7 | 27.8 | 58.5 | 29.3 | 220.4 | 213.7 | 213.7 | YES
| NG | 4 | 5 | 29 | 75 | 35.1 | 26.84 | 50 | 63.7 | 27.8 | 32.3 | 40.9 | 226.5 | 209.9 | 209.9 | NO
10 | OK | 34 | 35 | 35 | 76 | 96.7 | 6.03 | 50 | 63.7 | 27.8 | 56.7 | 30.6 | 220.9 | 213.5 | 213.5 | YES
11 | OK | 34 | 32 | 32 | 75 | 97.3 | 8.14 | 50 | 63.7 | 27.8 | 54.2 | 31.6 | 220.9 | 213.5 | 213.5 | YES
12 | OK | 21 | 15 | 31 | 55 | 44.8 | 3.36 | 50 | 63.7 | 27.8 | 59.8 | 29.3 | 220.2 | 213.7 | 213.7 | YES
| NG | 5 | 29 | 29 | 75 | 35.1 | 26.84 | 50 | 63.7 | 27.8 | 32.3 | 220 | 226.5 | 59.3 | 59.3 | NO
13 | OK | 35 | 36 | 36 | 76 | 97.9 | 6.03 | 50 | 63.7 | 27.8 | 56.7 | 29.4 | 220.9 | 213.7 | 213.7 | YES
14 | OK | 32 | 33 | 33 | 75 | 100.5 | 6.27 | 50 | 63.7 | 27.8 | 56.4 | 30.7 | 220.9 | 213.5 | 213.5 | YES
15 | OK | 15 | 30 | 31 | 55 | 44.8 | 3.2 | 50 | 63.7 | 27.8 | 60 | 29.3 | 220.2 | 213.7 | 213.7 | YES
| NG | 29 | 8 | 10 | 75 | 58.6 | 26.45 | 50 | 63.7 | 27.8 | 32.8 | 40.7 | 226.5 | 209.8 | 209.8 | NO
16 | OK | 36 | 37 | 37 | 76 | 111.3 | 3.57 | 50 | 63.7 | 27.8 | 59.5 | 29.4 | 220.3 | 213.7 | 213.7 | YES
17 | OK | 33 | 43 | 43 | 75 | 102.3 | 6.27 | 50 | 63.7 | 27.8 | 56.4 | 30.7 | 220.9 | 213.5 | 213.5 | YES
18 | OK | 30 | 31 | 31 | 55 | 44.8 | 3.2 | 50 | 63.7 | 27.8 | 60 | 29.3 | 220.2 | 213.7 | 213.7 | YES
19 | OK | 8 | 7 | 7 | 75 | 112.1 | 20.32 | 50 | 63.7 | 27.8 | 39.8 | 37.6 | 226.2 | 211.3 | 211.3 | YES
20 | OK | 8 | 9 | 10 | 75 | 58.6 | 3.98 | 50 | 63.7 | 27.8 | 59 | 28.4 | 220.4 | 213.7 | 213.7 | YES
21 | OK | 37 | 41 | 41 | 76 | 114.4 | 3.23 | 50 | 63.7 | 27.8 | 59.9 | 29.3 | 220.3 | 213.7 | 213.7 | YES
22 | OK | 43 | 27 | 27 | 75 | 109.6 | 6.27 | 50 | 63.7 | 27.8 | 56.4 | 30.7 | 220.9 | 213.5 | 213.5 | YES
23 | OK | 7 | 6 | 6 | 75 | 135.3 | 15.42 | 50 | 63.7 | 27.8 | 45.5 | 35.2 | 225.6 | 213.2 | 213.2 | YES
24 | OK | 7 | 47 | 47 | 75 | 120 | 0.23 | 50 | 63.7 | 27.8 | 63.4 | 27.9 | 220.2 | 213.7 | 213.7 | YES
25 | OK | 9 | 10 | 10 | 75 | 58.6 | 2.2 | 50 | 63.7 | 27.8 | 61.1 | 27.8 | 220.1 | 213.7 | 213.7 | YES
26 | OK | 41 | 42 | 42 | 76 | 126.5 | 3.23 | 50 | 63.7 | 27.8 | 59.9 | 29.3 | 220.3 | 213.7 | 213.7 | YES
27 | OK | 27 | 28 | 28 | 75 | 122 | 4.42 | 50 | 63.7 | 27.8 | 58.5 | 29.8 | 220.5 | 213.6 | 213.6 | YES
28 | OK | 47 | 48 | 48 | 75 | 121.1 | 0.23 | 50 | 63.7 | 27.8 | 63.4 | 27.8 | 220.2 | 213.7 | 213.7 | YES
29 | OK | 42 | 38 | 38 | 76 | 136.8 | 2.26 | 50 | 63.7 | 27.8 | 60.6 | 28.8 | 220.3 | 213.7 | 213.7 | YES
30 | OK | 28 | 20 | 20 | 75 | 133 | 1.17 | 50 | 63.7 | 27.8 | 62.3 | 28.3 | 220.2 | 213.7 | 213.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 59-020571
TR_B (available) | 38-023734
TR_A Rated kVA | 100
TR_B Rated kVA | 250
TR_A Baseline Loading% | 63.7
TR_B Baseline Loading% | 27.8
Total Scenarios Evaluated | 39
Feasible Scenarios | 30
--- Optimal Solution ---
Switch Parent Node | 16
Switch Child Node | 17
Tie Node (TR_A side) | 31
Tie Node (TR_B side) | 55
Tie Line Distance (m) | 44.8
Load Transferred (kW) | 24.91
TR_A Loading After (%) | 35
TR_B Loading After (%) | 31.4
Minimum Voltage (V) | 213.7