## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 52 | 13 | 25 | 16 | 9.3 | 29.92 | 50 | 63.7 | 37.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 52 | 16 | 20 | 61 | 60.6 | 25.04 | 50 | 63.7 | 37.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 13 | 14 | 18 | 61 | 127.4 | 2.98 | 50 | 63.7 | 37.8 | 60.2 | 40.1 | 220.2 | 214.1 | 214.1 | YES
| NG | 13 | 11 | 25 | 16 | 9.3 | 26.94 | 50 | 63.7 | 37.8 | 32.2 | 58.7 | 226.5 | 209.6 | 209.6 | NO
| NG | 16 | 17 | 20 | 61 | 60.6 | 24.91 | 50 | 63.7 | 37.8 | 35 | 56 | 222.2 | 203.5 | 203.5 | NO
2 | OK | 14 | 18 | 18 | 61 | 127.4 | 1.24 | 50 | 63.7 | 37.8 | 62.2 | 38.7 | 220.2 | 218.1 | 218.1 | YES
| NG | 11 | 12 | 25 | 16 | 9.3 | 26.9 | 50 | 63.7 | 37.8 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 37.8% (degenerate)
| NG | 17 | 19 | 20 | 61 | 60.6 | 22.52 | 50 | 63.7 | 37.8 | 37.7 | 55.7 | 222.2 | 204.6 | 204.6 | NO
| NG | 12 | 4 | 25 | 16 | 9.3 | 26.84 | 50 | 63.7 | 37.8 | 32.3 | 58.6 | 226.5 | 209.5 | 209.5 | NO
3 | OK | 19 | 34 | 20 | 61 | 60.6 | 14.17 | 50 | 63.7 | 37.8 | 47.3 | 48.8 | 221.5 | 212.1 | 212.1 | YES
| NG | 4 | 5 | 25 | 16 | 9.3 | 26.84 | 50 | 63.7 | 37.8 | 32.3 | 58.6 | 226.5 | 209.5 | 209.5 | NO
| NG | 34 | 35 | 57 | 64 | 91 | 6.03 | 50 | 63.7 | 37.8 | 56.7 | 42.9 | 220.9 | 201 | 201 | NO
4 | OK | 34 | 32 | 20 | 61 | 60.6 | 8.14 | 50 | 63.7 | 37.8 | 54.2 | 44 | 220.9 | 216.4 | 216.4 | YES
| NG | 5 | 29 | 25 | 16 | 9.3 | 26.84 | 50 | 63.7 | 37.8 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 37.8% (degenerate)
| NG | 35 | 36 | 57 | 64 | 91 | 6.03 | 50 | 63.7 | 37.8 | 56.7 | 40.7 | 220.9 | 209 | 209 | NO
5 | OK | 32 | 33 | 20 | 61 | 60.6 | 6.27 | 50 | 63.7 | 37.8 | 56.4 | 42.5 | 220.9 | 217.2 | 217.2 | YES
| NG | 29 | 8 | 25 | 16 | 9.3 | 26.45 | 50 | 63.7 | 37.8 | 32.8 | 58.3 | 226.5 | 209.5 | 209.5 | NO
| NG | 36 | 37 | 57 | 64 | 91 | 3.57 | 50 | 63.7 | 37.8 | 59.5 | 40.7 | 220.3 | 209 | 209 | NO
6 | OK | 33 | 43 | 20 | 61 | 60.6 | 6.27 | 50 | 63.7 | 37.8 | 56.4 | 42.5 | 220.9 | 217.2 | 217.2 | YES
7 | OK | 8 | 7 | 25 | 16 | 9.3 | 20.32 | 50 | 63.7 | 37.8 | 39.8 | 53.3 | 226.2 | 214.8 | 214.8 | YES
8 | OK | 8 | 9 | 9 | 62 | 114.4 | 3.98 | 50 | 63.7 | 37.8 | 59 | 38.9 | 220.4 | 215.5 | 215.5 | YES
9 | OK | 37 | 41 | 57 | 64 | 91 | 3.23 | 50 | 63.7 | 37.8 | 59.9 | 40.4 | 220.3 | 210 | 210 | YES
10 | OK | 43 | 27 | 20 | 61 | 60.6 | 6.27 | 50 | 63.7 | 37.8 | 56.4 | 42.5 | 220.9 | 217.2 | 217.2 | YES
11 | OK | 7 | 6 | 25 | 16 | 9.3 | 15.42 | 50 | 63.7 | 37.8 | 45.5 | 49.5 | 225.6 | 214.2 | 214.2 | YES
12 | OK | 7 | 47 | 48 | 61 | 54.6 | 0.23 | 50 | 63.7 | 37.8 | 63.4 | 38 | 220.2 | 218 | 218 | YES
13 | OK | 9 | 10 | 10 | 69 | 116.5 | 2.2 | 50 | 63.7 | 37.8 | 61.1 | 37.8 | 220.1 | 218.3 | 218.3 | YES
14 | OK | 41 | 42 | 57 | 64 | 91 | 3.23 | 50 | 63.7 | 37.8 | 59.9 | 40.4 | 220.3 | 210 | 210 | YES
15 | OK | 27 | 28 | 20 | 61 | 60.6 | 4.42 | 50 | 63.7 | 37.8 | 58.5 | 41.1 | 220.5 | 217.4 | 217.4 | YES
16 | OK | 6 | 26 | 25 | 16 | 9.3 | 11.52 | 50 | 63.7 | 37.8 | 50 | 46.5 | 225.4 | 215.7 | 215.7 | YES
17 | OK | 47 | 48 | 48 | 61 | 54.6 | 0.23 | 50 | 63.7 | 37.8 | 63.4 | 37.8 | 220.2 | 218.3 | 218.3 | YES
18 | OK | 42 | 38 | 57 | 64 | 91 | 2.26 | 50 | 63.7 | 37.8 | 60.6 | 39.6 | 220.3 | 212.8 | 212.8 | YES
19 | OK | 28 | 20 | 20 | 61 | 60.6 | 1.17 | 50 | 63.7 | 37.8 | 62.3 | 38.7 | 220.2 | 217.1 | 217.1 | YES
| NG | 26 | 1 | 25 | 16 | 9.3 | 9.06 | 50 | 63.7 | 37.8 | 0 | 44.7 | 6 | 215.2 | 6 | NO
20 | OK | 38 | 39 | 57 | 64 | 91 | 2.26 | 50 | 63.7 | 37.8 | 61 | 39.6 | 220.3 | 212.8 | 212.8 | YES
21 | OK | 1 | 0 | 25 | 16 | 9.3 | 7.65 | 50 | 63.7 | 37.8 | 54.6 | 43.6 | 222.8 | 215.1 | 215.1 | YES
22 | OK | 39 | 40 | 57 | 64 | 91 | 0.5 | 50 | 63.7 | 37.8 | 63.1 | 38.2 | 220.2 | 217.4 | 217.4 | YES
23 | OK | 0 | 22 | 25 | 16 | 9.3 | 5.48 | 50 | 63.7 | 37.8 | 57.1 | 41.9 | 223 | 217.6 | 217.6 | YES
24 | OK | 22 | 23 | 55 | 67 | 20.2 | 2.59 | 50 | 63.7 | 37.8 | 60.5 | 39.7 | 222 | 217 | 217 | YES
25 | OK | 22 | 51 | 25 | 16 | 9.3 | 2.78 | 50 | 63.7 | 37.8 | 60.3 | 39.9 | 221.2 | 218.7 | 218.7 | YES
26 | ** OPTIMAL ** | 23 | 49 | 55 | 67 | 20.2 | 1.52 | 50 | 63.7 | 37.8 | 61.8 | 38.9 | 222 | 218.8 | 218.8 | YES
27 | OK | 51 | 24 | 25 | 16 | 9.3 | 1.72 | 50 | 63.7 | 37.8 | 61.6 | 39.1 | 219.7 | 218.5 | 218.5 | YES
28 | OK | 49 | 50 | 55 | 67 | 20.2 | 0.18 | 50 | 63.7 | 37.8 | 63.4 | 37.9 | 220.1 | 218.4 | 218.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 59-020571
TR_B (available) | 49-005561
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 63.7
TR_B Baseline Loading% | 37.8
Total Scenarios Evaluated | 42
Feasible Scenarios | 28
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 49
Tie Node (TR_A side) | 55
Tie Node (TR_B side) | 67
Tie Line Distance (m) | 20.2
Load Transferred (kW) | 1.52
TR_A Loading After (%) | 61.8
TR_B Loading After (%) | 38.9
Minimum Voltage (V) | 218.8