## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 52 | 13 | 4 | 0 | 19 | 29.92 | 50 | 63.7 | 15 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 52 | 16 | 16 | 0 | 62.9 | 25.04 | 50 | 63.7 | 15 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 13 | 14 | 14 | 0 | 53.3 | 2.98 | 50 | 63.7 | 15 | 60.2 | 17.1 | 220.2 | 225.3 | 220.2 | YES
2 | OK | 13 | 11 | 4 | 0 | 19 | 26.94 | 50 | 63.7 | 15 | 32.2 | 35.5 | 226.5 | 212.5 | 212.5 | YES
3 | OK | 16 | 17 | 44 | 0 | 72.2 | 24.91 | 50 | 63.7 | 15 | 35 | 32.3 | 222.2 | 213.7 | 213.7 | YES
4 | OK | 14 | 18 | 18 | 0 | 60.2 | 1.24 | 50 | 63.7 | 15 | 62.2 | 15.9 | 220.2 | 224.9 | 220.2 | YES
| NG | 11 | 12 | 4 | 0 | 19 | 26.9 | 50 | 63.7 | 15 | 32.3 | 6340.5 | 226.5 | 221 | 221 | NO
5 | OK | 11 | 45 | 45 | 0 | 42.6 | 0.03 | 50 | 63.7 | 15 | 63.6 | 15 | 220.2 | 226.4 | 220.2 | YES
6 | OK | 17 | 19 | 34 | 0 | 96 | 22.52 | 50 | 63.7 | 15 | 37.7 | 32 | 222.2 | 214.5 | 214.5 | YES
| NG | 17 | 44 | 44 | 0 | 72.2 | 2.01 | 50 | 63.7 | 15 | 61.4 | 6246.5 | 220.2 | 223.5 | 220.2 | NO
7 | OK | 12 | 46 | 46 | 0 | 21.9 | 0.06 | 50 | 63.7 | 15 | 63.6 | 15 | 220.7 | 226.4 | 220.7 | YES
8 | OK | 12 | 4 | 4 | 0 | 19 | 26.84 | 50 | 63.7 | 15 | 32.3 | 35.4 | 226.5 | 212.5 | 212.5 | YES
9 | OK | 19 | 2 | 2 | 0 | 127.7 | 3.87 | 50 | 63.7 | 15 | 59.2 | 17.8 | 220.7 | 224.7 | 220.7 | YES
10 | OK | 19 | 34 | 34 | 0 | 96 | 14.17 | 50 | 63.7 | 15 | 47.3 | 25.6 | 221.5 | 219 | 219 | YES
11 | OK | 19 | 21 | 21 | 0 | 102.3 | 4.48 | 50 | 63.7 | 15 | 58.5 | 18.2 | 220.4 | 224.2 | 220.4 | YES
12 | OK | 4 | 5 | 29 | 0 | 35 | 26.84 | 50 | 63.7 | 15 | 32.3 | 35.4 | 226.5 | 213.3 | 213.3 | YES
13 | OK | 34 | 35 | 35 | 0 | 105.7 | 6.03 | 50 | 63.7 | 15 | 56.7 | 19.4 | 220.9 | 223.4 | 220.9 | YES
14 | OK | 34 | 32 | 32 | 0 | 97.7 | 8.14 | 50 | 63.7 | 15 | 54.2 | 21 | 220.9 | 221.7 | 220.9 | YES
15 | OK | 21 | 15 | 15 | 0 | 115.9 | 3.36 | 50 | 63.7 | 15 | 59.8 | 17.4 | 220.2 | 224 | 220.2 | YES
| NG | 5 | 29 | 29 | 0 | 35 | 26.84 | 50 | 63.7 | 15 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 15.0% (degenerate)
16 | OK | 35 | 36 | 36 | 0 | 107.6 | 6.03 | 50 | 63.7 | 15 | 56.7 | 17.6 | 220.9 | 223.1 | 220.9 | YES
17 | OK | 32 | 33 | 33 | 0 | 100.8 | 6.27 | 50 | 63.7 | 15 | 56.4 | 19.6 | 220.9 | 223.4 | 220.9 | YES
18 | OK | 15 | 30 | 31 | 0 | 118.9 | 3.2 | 50 | 63.7 | 15 | 60 | 17.3 | 220.2 | 225.4 | 220.2 | YES
19 | OK | 29 | 8 | 7 | 14 | 53.5 | 26.45 | 50 | 63.7 | 15 | 32.8 | 21.1 | 226.5 | 215.7 | 215.7 | YES
20 | OK | 36 | 37 | 37 | 0 | 124 | 3.57 | 50 | 63.7 | 15 | 59.5 | 17.6 | 220.3 | 223.1 | 220.3 | YES
21 | OK | 33 | 43 | 43 | 0 | 102.5 | 6.27 | 50 | 63.7 | 15 | 56.4 | 19.6 | 220.9 | 223.4 | 220.9 | YES
22 | OK | 30 | 31 | 31 | 0 | 118.9 | 3.2 | 50 | 63.7 | 15 | 60 | 17.3 | 220.2 | 225.4 | 220.2 | YES
23 | OK | 8 | 7 | 7 | 14 | 53.5 | 20.32 | 50 | 63.7 | 15 | 39.8 | 20.1 | 226.2 | 217.3 | 217.3 | YES
24 | OK | 8 | 9 | 10 | 2 | 56 | 3.98 | 50 | 63.7 | 15 | 59 | 16 | 220.4 | 226.6 | 220.4 | YES
25 | OK | 37 | 41 | 41 | 0 | 127.7 | 3.23 | 50 | 63.7 | 15 | 59.9 | 17.3 | 220.3 | 223 | 220.3 | YES
26 | OK | 43 | 27 | 27 | 0 | 109.8 | 6.27 | 50 | 63.7 | 15 | 56.4 | 19.6 | 220.9 | 223.5 | 220.9 | YES
27 | OK | 7 | 6 | 6 | 14 | 61.9 | 15.42 | 50 | 63.7 | 15 | 45.5 | 18.7 | 225.6 | 219.8 | 219.8 | YES
28 | OK | 7 | 47 | 47 | 14 | 92.9 | 0.23 | 50 | 63.7 | 15 | 63.4 | 15.1 | 220.2 | 226.1 | 220.2 | YES
29 | OK | 9 | 10 | 10 | 2 | 56 | 2.2 | 50 | 63.7 | 15 | 61.1 | 15 | 220.1 | 226.4 | 220.1 | YES
30 | OK | 41 | 42 | 42 | 0 | 141.7 | 3.23 | 50 | 63.7 | 15 | 59.9 | 17.3 | 220.3 | 223 | 220.3 | YES
31 | OK | 27 | 28 | 28 | 0 | 122.1 | 4.42 | 50 | 63.7 | 15 | 58.5 | 18.2 | 220.5 | 223.6 | 220.5 | YES
32 | OK | 6 | 26 | 26 | 14 | 76.9 | 11.52 | 50 | 63.7 | 15 | 50 | 17.4 | 225.4 | 221.9 | 221.9 | YES
33 | OK | 47 | 48 | 48 | 14 | 95.4 | 0.23 | 50 | 63.7 | 15 | 63.4 | 15 | 220.2 | 226.4 | 220.2 | YES
34 | OK | 28 | 20 | 20 | 14 | 131.6 | 1.17 | 50 | 63.7 | 15 | 62.3 | 15.2 | 220.2 | 225.9 | 220.2 | YES
| NG | 26 | 1 | 1 | 14 | 79.1 | 9.06 | 50 | 63.7 | 15 | 454.6 | 17.4 | 25.7 | 221.9 | 25.7 | NO
35 | OK | 1 | 0 | 55 | 14 | 95.1 | 7.65 | 50 | 63.7 | 15 | 54.6 | 16.4 | 222.8 | 223.8 | 222.8 | YES
36 | ** OPTIMAL ** | 0 | 22 | 55 | 14 | 95.1 | 5.48 | 50 | 63.7 | 15 | 57.1 | 16.4 | 223 | 223.8 | 223 | YES
37 | OK | 22 | 23 | 55 | 14 | 95.1 | 2.59 | 50 | 63.7 | 15 | 60.5 | 15.1 | 222 | 226.2 | 222 | YES
38 | OK | 22 | 51 | 51 | 14 | 105.9 | 2.78 | 50 | 63.7 | 15 | 60.3 | 16.2 | 221.2 | 224 | 221.2 | YES
39 | OK | 23 | 49 | 55 | 14 | 95.1 | 1.52 | 50 | 63.7 | 15 | 61.8 | 15.1 | 222 | 226.2 | 222 | YES
40 | OK | 51 | 24 | 24 | 14 | 108.1 | 1.72 | 50 | 63.7 | 15 | 61.6 | 16.2 | 219.7 | 224 | 219.7 | YES
41 | OK | 49 | 50 | 55 | 14 | 95.1 | 0.18 | 50 | 63.7 | 15 | 63.4 | 15.1 | 220.1 | 226.2 | 220.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 59-020571
TR_B (available) | 60-035538
TR_A Rated kVA | 100
TR_B Rated kVA | 160
TR_A Baseline Loading% | 63.7
TR_B Baseline Loading% | 15
Total Scenarios Evaluated | 47
Feasible Scenarios | 41
--- Optimal Solution ---
Switch Parent Node | 0
Switch Child Node | 22
Tie Node (TR_A side) | 55
Tie Node (TR_B side) | 14
Tie Line Distance (m) | 95.1
Load Transferred (kW) | 5.48
TR_A Loading After (%) | 57.1
TR_B Loading After (%) | 16.4
Minimum Voltage (V) | 223