## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 38 | 18 | 22 | 6 | 3.4 | 12.37 | 50 | 79.7 | 29.9 | 50.6 | 59.3 | 219.3 | 216 | 216 | YES
| NG | 38 | 8 | 8 | 6 | 182.5 | 21.69 | 50 | 79.7 | 29.9 | 29 | 84.7 | 219.6 | 195.5 | 195.5 | NO
2 | OK | 18 | 17 | 22 | 6 | 3.4 | 12.36 | 50 | 79.7 | 29.9 | 50.6 | 59.2 | 219.3 | 216 | 216 | YES
3 | OK | 8 | 9 | 9 | 6 | 189.3 | 3.29 | 50 | 79.7 | 29.9 | 72.1 | 37.7 | 217.7 | 220.2 | 217.7 | YES
| NG | 8 | 34 | 34 | 6 | 204.4 | 7.71 | 50 | 79.7 | 29.9 | 61.5 | 50 | 217.8 | 195.7 | 195.7 | NO
| NG | 8 | 12 | 12 | 6 | 195.7 | 10.69 | 50 | 79.7 | 29.9 | 54.7 | 56.4 | 217.7 | 202.9 | 202.9 | NO
4 | OK | 17 | 39 | 22 | 6 | 3.4 | 11.74 | 50 | 79.7 | 29.9 | 52.1 | 57.7 | 219.3 | 215.7 | 215.7 | YES
| NG | 9 | 10 | 10 | 6 | 189.5 | 3.29 | 50 | 79.7 | 29.9 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 29.9% (degenerate)
| NG | 34 | 35 | 35 | 6 | 232.4 | 7.11 | 50 | 79.7 | 29.9 | 62.9 | 48 | 217.8 | 200.6 | 200.6 | NO
| NG | 12 | 11 | 11 | 6 | 218 | 8.92 | 50 | 79.7 | 29.9 | 58.8 | 51.7 | 217.7 | 209 | 209 | NO
5 | OK | 39 | 23 | 22 | 6 | 3.4 | 11.45 | 50 | 79.7 | 29.9 | 52.1 | 57.1 | 219.3 | 215.6 | 215.6 | YES
| NG | 35 | 6 | 6 | 6 | 258.6 | 7.11 | 50 | 79.7 | 29.9 | 62.9 | 48 | 217.8 | 200.6 | 200.6 | NO
6 | OK | 11 | 13 | 13 | 6 | 238 | 7.66 | 50 | 79.7 | 29.9 | 61.7 | 48.5 | 217.7 | 213.3 | 213.3 | YES
7 | OK | 23 | 22 | 22 | 6 | 3.4 | 11.45 | 50 | 79.7 | 29.9 | 52.7 | 57.1 | 219.3 | 215.6 | 215.6 | YES
8 | OK | 13 | 16 | 16 | 6 | 259.6 | 7.37 | 50 | 79.7 | 29.9 | 62.3 | 47.7 | 217.7 | 214.3 | 214.3 | YES
9 | OK | 22 | 36 | 36 | 6 | 35 | 11.45 | 50 | 79.7 | 29.9 | 52.7 | 57.1 | 219.3 | 215.7 | 215.7 | YES
10 | OK | 36 | 37 | 37 | 6 | 60.6 | 11.35 | 50 | 79.7 | 29.9 | 53 | 56.8 | 219.3 | 216 | 216 | YES
11 | OK | 37 | 24 | 24 | 6 | 116.5 | 11.35 | 50 | 79.7 | 29.9 | 53 | 56.8 | 219.3 | 216.4 | 216.4 | YES
12 | OK | 24 | 25 | 25 | 6 | 162.5 | 10.28 | 50 | 79.7 | 29.9 | 55.4 | 54.2 | 219.1 | 216 | 216 | YES
13 | OK | 25 | 26 | 26 | 6 | 205.3 | 9.53 | 50 | 79.7 | 29.9 | 57.2 | 52.4 | 219.1 | 218.1 | 218.1 | YES
14 | ** OPTIMAL ** | 26 | 27 | 27 | 6 | 251.9 | 6.9 | 50 | 79.7 | 29.9 | 63.3 | 46.1 | 218.7 | 219.5 | 218.7 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-003308
TR_B (available) | 33-007396
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 79.7
TR_B Baseline Loading% | 29.9
Total Scenarios Evaluated | 21
Feasible Scenarios | 14
--- Optimal Solution ---
Switch Parent Node | 26
Switch Child Node | 27
Tie Node (TR_A side) | 27
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 251.9
Load Transferred (kW) | 6.9
TR_A Loading After (%) | 63.3
TR_B Loading After (%) | 46.1
Minimum Voltage (V) | 218.7