## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 48 | 53 | 53 | 14 | 173.3 | 9.94 | 50 | 72.2 | 61 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 53 | 51 | 51 | 13 | 182.7 | 9.74 | 50 | 72.2 | 61 | 48.5 | 74.2 | 215.1 | 190.4 | 190.4 | NO
| NG | 51 | 23 | 23 | 13 | 183.4 | 9.74 | 50 | 72.2 | 61 | 48.5 | 74.1 | 215.1 | 190.5 | 190.5 | NO
| NG | 3 | 4 | 15 | 12 | 1.8 | 17.69 | 50 | 72.2 | 61 | 30.5 | 82.6 | 211.5 | 210.8 | 210.8 | NO
| NG | 23 | 22 | 22 | 12 | 194.9 | 9.41 | 50 | 72.2 | 61 | 49.3 | 73.7 | 215 | 191.3 | 191.3 | NO
| NG | 4 | 5 | 15 | 12 | 1.8 | 17 | 50 | 72.2 | 61 | 32.1 | 81.8 | 211.5 | 210.3 | 210.3 | NO
1 | OK | 4 | 52 | 52 | 54 | 117 | 0.69 | 50 | 72.2 | 61 | 70.6 | 61.9 | 210.6 | 219.2 | 210.6 | YES
| NG | 5 | 6 | 15 | 12 | 1.8 | 16.49 | 50 | 72.2 | 61 | 32.1 | 81.1 | 211.5 | 211.6 | 211.5 | NO
2 | OK | 52 | 56 | 55 | 54 | 141.6 | 0.24 | 50 | 72.2 | 61 | 71.7 | 61.3 | 210.6 | 220.3 | 210.6 | YES
| NG | 6 | 7 | 15 | 12 | 1.8 | 16.16 | 50 | 72.2 | 61 | 34 | 80.7 | 211.5 | 211.4 | 211.4 | NO
3 | OK | 7 | 8 | 15 | 12 | 1.8 | 12.92 | 50 | 72.2 | 61 | 41.5 | 76.6 | 211.5 | 215.5 | 211.5 | YES
4 | ** OPTIMAL ** | 8 | 24 | 15 | 12 | 1.8 | 12.71 | 50 | 72.2 | 61 | 42 | 76.3 | 211.5 | 215.4 | 211.5 | YES
5 | OK | 24 | 38 | 15 | 12 | 1.8 | 12.23 | 50 | 72.2 | 61 | 43.1 | 75.5 | 211.3 | 215.3 | 211.3 | YES
6 | OK | 38 | 37 | 15 | 12 | 1.8 | 12.04 | 50 | 72.2 | 61 | 43.5 | 75.5 | 211.2 | 215.3 | 211.2 | YES
7 | OK | 37 | 36 | 15 | 12 | 1.8 | 12.01 | 50 | 72.2 | 61 | 43.6 | 75.5 | 211.2 | 215.3 | 211.2 | YES
8 | OK | 36 | 35 | 15 | 12 | 1.8 | 10.07 | 50 | 72.2 | 61 | 48.1 | 73.1 | 211.2 | 218.9 | 211.2 | YES
9 | OK | 35 | 34 | 15 | 12 | 1.8 | 9.03 | 50 | 72.2 | 61 | 50.6 | 71.8 | 211.2 | 219.2 | 211.2 | YES
10 | OK | 34 | 33 | 15 | 12 | 1.8 | 6.85 | 50 | 72.2 | 61 | 55.7 | 69.2 | 211.2 | 220.3 | 211.2 | YES
11 | OK | 33 | 31 | 15 | 12 | 1.8 | 4.8 | 50 | 72.2 | 61 | 60.6 | 66.7 | 211 | 220.3 | 211 | YES
| NG | 31 | 29 | 29 | 12 | 90.4 | 3.97 | 50 | 72.2 | 61 | 0 | 65.7 | 6 | 220.4 | 6 | NO
12 | OK | 31 | 17 | 15 | 12 | 1.8 | 0.71 | 50 | 72.2 | 61 | 70.5 | 61.9 | 210.6 | 220.8 | 210.6 | YES
13 | OK | 29 | 30 | 30 | 12 | 95.6 | 3.97 | 50 | 72.2 | 61 | 62.6 | 65.7 | 211 | 220.4 | 211 | YES
14 | OK | 17 | 16 | 15 | 12 | 1.8 | 0.35 | 50 | 72.2 | 61 | 71.4 | 61.4 | 210.6 | 220.8 | 210.6 | YES
15 | OK | 30 | 27 | 27 | 12 | 113.5 | 3.97 | 50 | 72.2 | 61 | 62.6 | 65.7 | 211 | 220.4 | 211 | YES
16 | OK | 27 | 28 | 43 | 11 | 115.6 | 3.37 | 50 | 72.2 | 61 | 64.1 | 65 | 211 | 220.1 | 211 | YES
17 | OK | 28 | 10 | 10 | 12 | 144.1 | 2.84 | 50 | 72.2 | 61 | 65.5 | 64.4 | 211 | 220.4 | 211 | YES
18 | OK | 10 | 9 | 9 | 12 | 166.2 | 1.61 | 50 | 72.2 | 61 | 68.4 | 62.9 | 211 | 220.3 | 211 | YES
19 | OK | 9 | 39 | 39 | 12 | 181.6 | 1.07 | 50 | 72.2 | 61 | 69.7 | 62.3 | 211 | 220.3 | 211 | YES
20 | OK | 39 | 25 | 25 | 12 | 199.1 | 0.98 | 50 | 72.2 | 61 | 69.9 | 62.2 | 211 | 220.2 | 211 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-003312
TR_B (available) | 40-020780
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 72.2
TR_B Baseline Loading% | 61
Total Scenarios Evaluated | 29
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 8
Switch Child Node | 24
Tie Node (TR_A side) | 15
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 1.8
Load Transferred (kW) | 12.71
TR_A Loading After (%) | 42
TR_B Loading After (%) | 76.3
Minimum Voltage (V) | 211.5