## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 22 | 10 | 16 | 4.3 | 11.36 | 50 | 81.7 | 64.5 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | ** OPTIMAL ** | 22 | 15 | 10 | 16 | 4.3 | 11.36 | 50 | 81.7 | 64.5 | 55.4 | 70.8 | 211.4 | 211.4 | 211.4 | YES
2 | OK | 15 | 16 | 10 | 16 | 4.3 | 10.48 | 50 | 81.7 | 64.5 | 57.4 | 69.7 | 210.9 | 212.7 | 210.9 | YES
3 | OK | 16 | 9 | 10 | 16 | 4.3 | 10.48 | 50 | 81.7 | 64.5 | 57.4 | 69.7 | 210.9 | 212.7 | 210.9 | YES
| NG | 9 | 20 | 19 | 4 | 14.2 | 10.48 | 50 | 81.7 | 64.5 | 57.4 | 79.8 | 210.9 | 186.3 | 186.3 | NO
| NG | 20 | 19 | 19 | 4 | 14.2 | 9.69 | 50 | 81.7 | 64.5 | 59.2 | 78.5 | 210.9 | 188.3 | 188.3 | NO
| NG | 19 | 18 | 17 | 43 | 37.8 | 9.23 | 50 | 81.7 | 64.5 | 60.2 | 77.5 | 210.9 | 192.9 | 192.9 | NO
| NG | 18 | 17 | 17 | 43 | 37.8 | 7.27 | 50 | 81.7 | 64.5 | 64.7 | 74.5 | 210.9 | 197.6 | 197.6 | NO
| NG | 17 | 24 | 24 | 43 | 37.9 | 3.48 | 50 | 81.7 | 64.5 | 73.5 | 69.1 | 211 | 206.3 | 206.3 | NO
| NG | 24 | 23 | 23 | 43 | 39.9 | 3.48 | 50 | 81.7 | 64.5 | 73.5 | 69.1 | 211 | 206.4 | 206.4 | NO
| NG | 23 | 27 | 8 | 42 | 51.3 | 1.3 | 50 | 81.7 | 64.5 | 78.7 | 66.2 | 211 | 209.3 | 209.3 | NO
| NG | 23 | 28 | 28 | 43 | 82.2 | 2.18 | 50 | 81.7 | 64.5 | 76.6 | 67.4 | 211 | 209 | 209 | NO
| NG | 27 | 8 | 8 | 42 | 51.3 | 1.3 | 50 | 81.7 | 64.5 | 78.7 | 66.2 | 211 | 209.3 | 209.3 | NO
4 | OK | 28 | 29 | 29 | 43 | 88 | 2.18 | 50 | 81.7 | 64.5 | 76.6 | 66.2 | 211 | 210.4 | 210.4 | YES
5 | OK | 29 | 30 | 30 | 43 | 100.4 | 0.95 | 50 | 81.7 | 64.5 | 79.5 | 65.7 | 211 | 210.9 | 210.9 | YES
6 | OK | 30 | 31 | 31 | 43 | 113.7 | 0.95 | 50 | 81.7 | 64.5 | 79.5 | 65.7 | 211 | 210.9 | 210.9 | YES
7 | OK | 31 | 32 | 32 | 43 | 126.5 | 0.95 | 50 | 81.7 | 64.5 | 79.5 | 65.7 | 211 | 210.9 | 210.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-003668
TR_B (available) | 57-002164
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 81.7
TR_B Baseline Loading% | 64.5
Total Scenarios Evaluated | 17
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 22
Switch Child Node | 15
Tie Node (TR_A side) | 10
Tie Node (TR_B side) | 16
Tie Line Distance (m) | 4.3
Load Transferred (kW) | 11.36
TR_A Loading After (%) | 55.4
TR_B Loading After (%) | 70.8
Minimum Voltage (V) | 211.4