## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | ** OPTIMAL ** | 35 | 22 | 7 | 12 | 138.3 | 11.36 | 50 | 81.7 | 50 | 55.4 | 65.1 | 211.4 | 215.2 | 211.4 | YES
2 | OK | 22 | 15 | 7 | 12 | 138.3 | 11.36 | 50 | 81.7 | 50 | 55.4 | 65.1 | 211.4 | 215.2 | 211.4 | YES
3 | OK | 15 | 16 | 7 | 12 | 138.3 | 10.48 | 50 | 81.7 | 50 | 57.4 | 65.1 | 210.9 | 215.2 | 210.9 | YES
4 | OK | 16 | 9 | 7 | 12 | 138.3 | 10.48 | 50 | 81.7 | 50 | 57.4 | 65.1 | 210.9 | 215.2 | 210.9 | YES
5 | OK | 9 | 20 | 7 | 12 | 138.3 | 10.48 | 50 | 81.7 | 50 | 57.4 | 65.1 | 210.9 | 215.2 | 210.9 | YES
6 | OK | 20 | 19 | 7 | 12 | 138.3 | 9.69 | 50 | 81.7 | 50 | 59.2 | 63.1 | 210.9 | 217.4 | 210.9 | YES
7 | OK | 19 | 18 | 7 | 12 | 138.3 | 9.23 | 50 | 81.7 | 50 | 60.2 | 61.9 | 210.9 | 218.5 | 210.9 | YES
8 | OK | 18 | 17 | 7 | 12 | 138.3 | 7.27 | 50 | 81.7 | 50 | 64.7 | 58.8 | 210.9 | 221.4 | 210.9 | YES
9 | OK | 17 | 24 | 7 | 12 | 138.3 | 3.48 | 50 | 81.7 | 50 | 73.5 | 57.4 | 211 | 222 | 211 | YES
10 | OK | 24 | 23 | 7 | 12 | 138.3 | 3.48 | 50 | 81.7 | 50 | 73.5 | 57.4 | 211 | 222 | 211 | YES
11 | OK | 23 | 27 | 7 | 12 | 138.3 | 1.3 | 50 | 81.7 | 50 | 78.7 | 53 | 211 | 221.7 | 211 | YES
12 | OK | 23 | 28 | 26 | 36 | 140.8 | 2.18 | 50 | 81.7 | 50 | 76.6 | 55.1 | 211 | 221.7 | 211 | YES
13 | OK | 27 | 8 | 7 | 12 | 138.3 | 1.3 | 50 | 81.7 | 50 | 78.7 | 53 | 211 | 221.7 | 211 | YES
14 | OK | 28 | 29 | 26 | 36 | 140.8 | 2.18 | 50 | 81.7 | 50 | 76.6 | 53 | 211 | 221.5 | 211 | YES
15 | OK | 29 | 30 | 26 | 36 | 140.8 | 0.95 | 50 | 81.7 | 50 | 79.5 | 52.2 | 211 | 221.9 | 211 | YES
16 | OK | 30 | 31 | 26 | 36 | 140.8 | 0.95 | 50 | 81.7 | 50 | 79.5 | 52.2 | 211 | 221.9 | 211 | YES
17 | OK | 31 | 32 | 26 | 36 | 140.8 | 0.95 | 50 | 81.7 | 50 | 79.5 | 52.2 | 211 | 221.9 | 211 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-003668
TR_B (available) | 57-010684
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 81.7
TR_B Baseline Loading% | 50
Total Scenarios Evaluated | 17
Feasible Scenarios | 17
--- Optimal Solution ---
Switch Parent Node | 35
Switch Child Node | 22
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 12
Tie Line Distance (m) | 138.3
Load Transferred (kW) | 11.36
TR_A Loading After (%) | 55.4
TR_B Loading After (%) | 65.1
Minimum Voltage (V) | 211.4