## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 22 | 7 | 6 | 34.4 | 11.36 | 50 | 81.7 | 37.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 22 | 15 | 7 | 6 | 34.4 | 11.36 | 50 | 81.7 | 37.7 | 55.4 | 52.1 | 211.4 | 205.6 | 205.6 | NO
| NG | 15 | 16 | 7 | 6 | 34.4 | 10.48 | 50 | 81.7 | 37.7 | 57.4 | 50.9 | 210.9 | 207.9 | 207.9 | NO
| NG | 16 | 9 | 7 | 6 | 34.4 | 10.48 | 50 | 81.7 | 37.7 | 57.4 | 50.9 | 210.9 | 207.9 | 207.9 | NO
| NG | 9 | 20 | 7 | 6 | 34.4 | 10.48 | 50 | 81.7 | 37.7 | 57.4 | 50.9 | 210.9 | 207.9 | 207.9 | NO
| NG | 20 | 19 | 7 | 6 | 34.4 | 9.69 | 50 | 81.7 | 37.7 | 59.2 | 49.8 | 210.9 | 209.7 | 209.7 | NO
1 | OK | 19 | 18 | 7 | 6 | 34.4 | 9.23 | 50 | 81.7 | 37.7 | 60.2 | 49.2 | 210.9 | 210.7 | 210.7 | YES
2 | OK | 18 | 17 | 7 | 6 | 34.4 | 7.27 | 50 | 81.7 | 37.7 | 64.7 | 46.6 | 210.9 | 214.3 | 210.9 | YES
3 | OK | 17 | 24 | 7 | 6 | 34.4 | 3.48 | 50 | 81.7 | 37.7 | 73.5 | 41.9 | 211 | 220.7 | 211 | YES
4 | OK | 24 | 23 | 7 | 6 | 34.4 | 3.48 | 50 | 81.7 | 37.7 | 73.5 | 41.9 | 211 | 220.7 | 211 | YES
5 | ** OPTIMAL ** | 23 | 27 | 7 | 6 | 34.4 | 1.3 | 50 | 81.7 | 37.7 | 78.7 | 39.3 | 211 | 222.7 | 211 | YES
6 | OK | 27 | 8 | 7 | 6 | 34.4 | 1.3 | 50 | 81.7 | 37.7 | 78.7 | 39.3 | 211 | 222.7 | 211 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-003668
TR_B (available) | 58-016115
TR_A Rated kVA | 50
TR_B Rated kVA | 100
TR_A Baseline Loading% | 81.7
TR_B Baseline Loading% | 37.7
Total Scenarios Evaluated | 12
Feasible Scenarios | 6
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 27
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 6
Tie Line Distance (m) | 34.4
Load Transferred (kW) | 1.3
TR_A Loading After (%) | 78.7
TR_B Loading After (%) | 39.3
Minimum Voltage (V) | 211