## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 6 | 5 | 34 | 17 | 5.2 | 5.93 | 50 | 81.7 | 43.8 | 67.2 | 49.1 | 220.1 | 217.4 | 217.4 | YES
2 | ** OPTIMAL ** | 6 | 37 | 37 | 17 | 144.7 | 5.12 | 50 | 81.7 | 43.8 | 69.1 | 43.8 | 219.9 | 218.5 | 218.5 | YES
3 | OK | 5 | 4 | 34 | 17 | 5.2 | 4.58 | 50 | 81.7 | 43.8 | 70.5 | 49.1 | 217.8 | 217.4 | 217.4 | YES
4 | OK | 4 | 0 | 34 | 17 | 5.2 | 4.3 | 50 | 81.7 | 43.8 | 71.2 | 49.1 | 217.4 | 217.4 | 217.4 | YES
5 | OK | 0 | 1 | 34 | 17 | 5.2 | 3.99 | 50 | 81.7 | 43.8 | 71.9 | 49.1 | 216.8 | 217.4 | 216.8 | YES
6 | OK | 1 | 33 | 34 | 17 | 5.2 | 3.57 | 50 | 81.7 | 43.8 | 72.9 | 48.7 | 216.2 | 217.5 | 216.2 | YES
7 | OK | 33 | 34 | 34 | 17 | 5.2 | 2.68 | 50 | 81.7 | 43.8 | 75.1 | 47.7 | 215 | 217.7 | 215 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-003668
TR_B (available) | 62-007340
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 81.7
TR_B Baseline Loading% | 43.8
Total Scenarios Evaluated | 7
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 37
Tie Node (TR_A side) | 37
Tie Node (TR_B side) | 17
Tie Line Distance (m) | 144.7
Load Transferred (kW) | 5.12
TR_A Loading After (%) | 69.1
TR_B Loading After (%) | 43.8
Minimum Voltage (V) | 218.5