## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 21 | 6 | 2 | 4.2 | 23.53 | 50 | 81.7 | 38.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 21 | 36 | 6 | 2 | 4.2 | 22.43 | 50 | 81.7 | 38.2 | 28.9 | 50.1 | 222.9 | 195 | 195 | NO
| NG | 36 | 14 | 6 | 2 | 4.2 | 20.9 | 50 | 81.7 | 38.2 | 32.4 | 49.2 | 222.9 | 199.3 | 199.3 | NO
| NG | 14 | 13 | 6 | 2 | 4.2 | 20.59 | 50 | 81.7 | 38.2 | 33.1 | 49 | 222.7 | 199.1 | 199.1 | NO
| NG | 13 | 12 | 6 | 2 | 4.2 | 18.6 | 50 | 81.7 | 38.2 | 37.7 | 48 | 222.3 | 198.4 | 198.4 | NO
| NG | 12 | 11 | 6 | 2 | 4.2 | 12.47 | 50 | 81.7 | 38.2 | 51.9 | 44.9 | 220.9 | 196.1 | 196.1 | NO
| NG | 11 | 40 | 6 | 2 | 4.2 | 11.84 | 50 | 81.7 | 38.2 | 53.3 | 44.6 | 220.6 | 195.7 | 195.7 | NO
| NG | 40 | 6 | 6 | 2 | 4.2 | 11.05 | 50 | 81.7 | 38.2 | 54.1 | 44.1 | 220.6 | 197 | 197 | NO
1 | OK | 6 | 5 | 5 | 2 | 38.6 | 5.93 | 50 | 81.7 | 38.2 | 67.2 | 41.2 | 220.1 | 210.2 | 210.2 | YES
2 | OK | 6 | 37 | 37 | 2 | 20.8 | 5.12 | 50 | 81.7 | 38.2 | 69.1 | 40.8 | 219.9 | 210.1 | 210.1 | YES
3 | ** OPTIMAL ** | 5 | 4 | 3 | 2 | 69.9 | 4.58 | 50 | 81.7 | 38.2 | 70.5 | 39.8 | 217.8 | 212.5 | 212.5 | YES
4 | OK | 37 | 38 | 38 | 2 | 70.3 | 1.1 | 50 | 81.7 | 38.2 | 78.9 | 38.7 | 213 | 212.5 | 212.5 | YES
5 | OK | 4 | 0 | 3 | 2 | 69.9 | 4.3 | 50 | 81.7 | 38.2 | 71.2 | 39.7 | 217.4 | 212.5 | 212.5 | YES
6 | OK | 38 | 39 | 39 | 2 | 72.3 | 1.1 | 50 | 81.7 | 38.2 | 78.9 | 38.2 | 213 | 212.5 | 212.5 | YES
7 | OK | 0 | 1 | 1 | 2 | 107.2 | 3.99 | 50 | 81.7 | 38.2 | 71.9 | 40.2 | 216.8 | 212.5 | 212.5 | YES
8 | OK | 1 | 33 | 33 | 2 | 138.1 | 3.57 | 50 | 81.7 | 38.2 | 72.9 | 40 | 216.2 | 212.5 | 212.5 | YES
9 | OK | 33 | 34 | 34 | 2 | 140.7 | 2.68 | 50 | 81.7 | 38.2 | 75.1 | 38.8 | 215 | 212.5 | 212.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-003668
TR_B (available) | 66-025633
TR_A Rated kVA | 50
TR_B Rated kVA | 250
TR_A Baseline Loading% | 81.7
TR_B Baseline Loading% | 38.2
Total Scenarios Evaluated | 17
Feasible Scenarios | 9
--- Optimal Solution ---
Switch Parent Node | 5
Switch Child Node | 4
Tie Node (TR_A side) | 3
Tie Node (TR_B side) | 2
Tie Line Distance (m) | 69.9
Load Transferred (kW) | 4.58
TR_A Loading After (%) | 70.5
TR_B Loading After (%) | 39.8
Minimum Voltage (V) | 212.5