## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 35 | 36 | 36 | 12 | 84.3 | 18.66 | 50 | 115.9 | 30.7 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 36 | 4 | 4 | 10 | 146.7 | 18.66 | 50 | 115.9 | 30.7 | 71.8 | 77.1 | 219.5 | 199 | 199 | NO
| NG | 16 | 5 | 5 | 10 | 63.1 | 24.11 | 50 | 115.9 | 30.7 | 58.1 | 84.5 | 213.6 | 213.2 | 213.2 | NO
1 | OK | 5 | 6 | 6 | 10 | 77.9 | 19.72 | 50 | 115.9 | 30.7 | 69.7 | 77.2 | 212 | 214.9 | 212 | YES
2 | ** OPTIMAL ** | 6 | 7 | 7 | 10 | 90.3 | 19.72 | 50 | 115.9 | 30.7 | 69.7 | 77.2 | 212 | 215 | 212 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-003718
TR_B (available) | 62-002889
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 115.9
TR_B Baseline Loading% | 30.7
Total Scenarios Evaluated | 5
Feasible Scenarios | 2
--- Optimal Solution ---
Switch Parent Node | 6
Switch Child Node | 7
Tie Node (TR_A side) | 7
Tie Node (TR_B side) | 10
Tie Line Distance (m) | 90.3
Load Transferred (kW) | 19.72
TR_A Loading After (%) | 69.7
TR_B Loading After (%) | 77.2
Minimum Voltage (V) | 212