## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 2 | 14 | 60 | 46 | 63.2 | 6.26 | 50 | 76.3 | 31.9 | 61.9 | 40.3 | 217.1 | 213.8 | 213.8 | YES
2 | OK | 14 | 13 | 60 | 46 | 63.2 | 6.26 | 50 | 76.3 | 31.9 | 61.9 | 40.3 | 217.1 | 213.8 | 213.8 | YES
3 | OK | 13 | 40 | 60 | 46 | 63.2 | 6.26 | 50 | 76.3 | 31.9 | 61.9 | 40.3 | 217.1 | 213.8 | 213.8 | YES
4 | OK | 40 | 42 | 60 | 46 | 63.2 | 5.79 | 50 | 76.3 | 31.9 | 62.9 | 38.3 | 216.9 | 216 | 216 | YES
5 | OK | 42 | 41 | 60 | 46 | 63.2 | 4.65 | 50 | 76.3 | 31.9 | 65.6 | 38.3 | 216.9 | 216 | 216 | YES
6 | OK | 41 | 56 | 60 | 46 | 63.2 | 3.27 | 50 | 76.3 | 31.9 | 68.7 | 38.3 | 216.9 | 216 | 216 | YES
7 | OK | 56 | 74 | 60 | 46 | 63.2 | 3.27 | 50 | 76.3 | 31.9 | 68.7 | 38.3 | 216.9 | 216 | 216 | YES
8 | OK | 74 | 75 | 60 | 46 | 63.2 | 2.68 | 50 | 76.3 | 31.9 | 70.1 | 35.8 | 216.6 | 218.5 | 216.6 | YES
9 | OK | 75 | 76 | 60 | 46 | 63.2 | 1.89 | 50 | 76.3 | 31.9 | 71.9 | 35.8 | 216.6 | 218.5 | 216.6 | YES
10 | OK | 76 | 59 | 60 | 46 | 63.2 | 0.98 | 50 | 76.3 | 31.9 | 74 | 35.8 | 216.6 | 218.5 | 216.6 | YES
11 | ** OPTIMAL ** | 59 | 60 | 60 | 46 | 63.2 | 0.95 | 50 | 76.3 | 31.9 | 74.1 | 35.8 | 216.6 | 218.5 | 216.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-004364
TR_B (available) | 38-012241
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 76.3
TR_B Baseline Loading% | 31.9
Total Scenarios Evaluated | 11
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 59
Switch Child Node | 60
Tie Node (TR_A side) | 60
Tie Node (TR_B side) | 46
Tie Line Distance (m) | 63.2
Load Transferred (kW) | 0.95
TR_A Loading After (%) | 74.1
TR_B Loading After (%) | 35.8
Minimum Voltage (V) | 216.6