## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 0 | 1 | 43 | 8 | 8.1 | 7.01 | 50 | 76.3 | 11.4 | 59.9 | 34 | 218.1 | 221.9 | 218.1 | YES
2 | OK | 1 | 39 | 43 | 8 | 8.1 | 5.31 | 50 | 76.3 | 11.4 | 63.8 | 29.8 | 218.1 | 224.5 | 218.1 | YES
3 | OK | 39 | 80 | 43 | 8 | 8.1 | 5.31 | 50 | 76.3 | 11.4 | 63.8 | 29.8 | 218.1 | 224.5 | 218.1 | YES
4 | OK | 80 | 22 | 43 | 8 | 8.1 | 4.78 | 50 | 76.3 | 11.4 | 65 | 29.8 | 218.1 | 224.5 | 218.1 | YES
5 | OK | 22 | 23 | 43 | 8 | 8.1 | 4.78 | 50 | 76.3 | 11.4 | 65 | 29.8 | 218.1 | 224.5 | 218.1 | YES
6 | ** OPTIMAL ** | 23 | 36 | 43 | 8 | 8.1 | 4.78 | 50 | 76.3 | 11.4 | 65 | 29.8 | 218.1 | 224.5 | 218.1 | YES
7 | OK | 36 | 37 | 37 | 8 | 66.2 | 1.92 | 50 | 76.3 | 11.4 | 71.7 | 18.7 | 217.7 | 225.5 | 217.7 | YES
8 | OK | 36 | 4 | 43 | 8 | 8.1 | 2.86 | 50 | 76.3 | 11.4 | 69.5 | 22.4 | 216.6 | 224.3 | 216.6 | YES
9 | OK | 37 | 20 | 20 | 8 | 83.9 | 0.51 | 50 | 76.3 | 11.4 | 75 | 13.3 | 216.6 | 226.5 | 216.6 | YES
10 | OK | 4 | 5 | 5 | 8 | 52.5 | 0.29 | 50 | 76.3 | 11.4 | 75.6 | 12.5 | 216.4 | 226.6 | 216.4 | YES
11 | OK | 4 | 34 | 34 | 8 | 64.3 | 2.57 | 50 | 76.3 | 11.4 | 70.2 | 21.3 | 216.4 | 224.3 | 216.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-004364
TR_B (available) | 61-004364
TR_A Rated kVA | 50
TR_B Rated kVA | 30
TR_A Baseline Loading% | 76.3
TR_B Baseline Loading% | 11.4
Total Scenarios Evaluated | 11
Feasible Scenarios | 11
--- Optimal Solution ---
Switch Parent Node | 23
Switch Child Node | 36
Tie Node (TR_A side) | 43
Tie Node (TR_B side) | 8
Tie Line Distance (m) | 8.1
Load Transferred (kW) | 4.78
TR_A Loading After (%) | 65
TR_B Loading After (%) | 29.8
Minimum Voltage (V) | 218.1