## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 2 | 0 | 69 | 21 | 104.8 | 21.29 | 50 | 76.3 | 18.7 | 26.5 | 31.8 | 227.2 | 206.5 | 206.5 | NO
1 | OK | 0 | 26 | 54 | 21 | 106.9 | 14.24 | 50 | 76.3 | 18.7 | 42.8 | 31.2 | 224 | 213.7 | 213.7 | YES
2 | OK | 26 | 25 | 54 | 21 | 106.9 | 14.24 | 50 | 76.3 | 18.7 | 42.8 | 31.2 | 224 | 213.7 | 213.7 | YES
3 | OK | 25 | 48 | 54 | 21 | 106.9 | 14.24 | 50 | 76.3 | 18.7 | 42.8 | 31.2 | 224 | 213.7 | 213.7 | YES
4 | OK | 48 | 33 | 54 | 21 | 106.9 | 14.24 | 50 | 76.3 | 18.7 | 42.8 | 31.2 | 224 | 213.7 | 213.7 | YES
5 | OK | 33 | 32 | 54 | 21 | 106.9 | 12.91 | 50 | 76.3 | 18.7 | 45.9 | 31.2 | 223.2 | 213.7 | 213.7 | YES
6 | OK | 32 | 27 | 54 | 21 | 106.9 | 12.91 | 50 | 76.3 | 18.7 | 0 | 31.2 | 230.9 | 213.7 | 213.7 | YES
7 | OK | 27 | 12 | 54 | 21 | 106.9 | 11.11 | 50 | 76.3 | 18.7 | 50 | 31.2 | 223.2 | 213.7 | 213.7 | YES
8 | OK | 12 | 10 | 54 | 21 | 106.9 | 10.34 | 50 | 76.3 | 18.7 | 51.8 | 29.5 | 223.1 | 216 | 216 | YES
9 | OK | 10 | 8 | 54 | 21 | 106.9 | 9.68 | 50 | 76.3 | 18.7 | 53.3 | 27.8 | 223.2 | 218.2 | 218.2 | YES
10 | OK | 8 | 11 | 54 | 21 | 106.9 | 5.72 | 50 | 76.3 | 18.7 | 62.7 | 20 | 218.4 | 225.6 | 218.4 | YES
11 | OK | 11 | 44 | 54 | 21 | 106.9 | 4.09 | 50 | 76.3 | 18.7 | 66.5 | 20 | 218.6 | 225.6 | 218.6 | YES
12 | OK | 44 | 77 | 54 | 21 | 106.9 | 4.09 | 50 | 76.3 | 18.7 | 66.5 | 20 | 218.6 | 225.6 | 218.6 | YES
13 | OK | 77 | 55 | 54 | 21 | 106.9 | 3.68 | 50 | 76.3 | 18.7 | 67.4 | 20 | 218.7 | 225.6 | 218.7 | YES
14 | ** OPTIMAL ** | 55 | 50 | 54 | 21 | 106.9 | 3.68 | 50 | 76.3 | 18.7 | 67.4 | 20 | 218.7 | 225.6 | 218.7 | YES
15 | OK | 50 | 49 | 54 | 21 | 106.9 | 0.97 | 50 | 76.3 | 18.7 | 73.9 | 20 | 217.5 | 225.6 | 217.5 | YES
16 | OK | 49 | 52 | 54 | 21 | 106.9 | 0.97 | 50 | 76.3 | 18.7 | 73.9 | 20 | 217.5 | 225.6 | 217.5 | YES
17 | OK | 52 | 53 | 54 | 21 | 106.9 | 0.56 | 50 | 76.3 | 18.7 | 74.9 | 20 | 216 | 225.6 | 216 | YES
18 | OK | 53 | 54 | 54 | 21 | 106.9 | 0.02 | 50 | 76.3 | 18.7 | 74.9 | 18.7 | 216 | 225.6 | 216 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-004364
TR_B (available) | 67-037562
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 76.3
TR_B Baseline Loading% | 18.7
Total Scenarios Evaluated | 19
Feasible Scenarios | 18
--- Optimal Solution ---
Switch Parent Node | 55
Switch Child Node | 50
Tie Node (TR_A side) | 54
Tie Node (TR_B side) | 21
Tie Line Distance (m) | 106.9
Load Transferred (kW) | 3.68
TR_A Loading After (%) | 67.4
TR_B Loading After (%) | 20
Minimum Voltage (V) | 218.7