## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 34 | 32 | 36 | 39 | 42.2 | 21.05 | 50 | 71.3 | 40.2 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 32 | 2 | 36 | 39 | 42.2 | 20.46 | 50 | 71.3 | 40.2 | 23.8 | 55.2 | 221.9 | 212.5 | 212.5 | YES
2 | ** OPTIMAL ** | 2 | 33 | 17 | 47 | 100.8 | 3.98 | 50 | 71.3 | 40.2 | 62 | 43.3 | 220.4 | 215 | 215 | YES
3 | OK | 2 | 3 | 36 | 39 | 42.2 | 15.42 | 50 | 71.3 | 40.2 | 35.4 | 51.5 | 221.9 | 212.7 | 212.7 | YES
4 | OK | 33 | 31 | 17 | 47 | 100.8 | 3.55 | 50 | 71.3 | 40.2 | 63 | 42.9 | 220.4 | 215 | 215 | YES
5 | OK | 3 | 4 | 55 | 48 | 65.8 | 1.66 | 50 | 71.3 | 40.2 | 67.4 | 41.5 | 220.1 | 213.4 | 213.4 | YES
6 | OK | 3 | 7 | 7 | 86 | 144.5 | 1.36 | 50 | 71.3 | 40.2 | 68.1 | 41.2 | 220.4 | 214.5 | 214.5 | YES
7 | OK | 3 | 9 | 36 | 39 | 42.2 | 12.24 | 50 | 71.3 | 40.2 | 42.4 | 49.2 | 221.8 | 213.2 | 213.2 | YES
8 | OK | 31 | 16 | 17 | 47 | 100.8 | 2.92 | 50 | 71.3 | 40.2 | 64.4 | 42.4 | 220.4 | 214.9 | 214.9 | YES
9 | OK | 4 | 5 | 55 | 48 | 65.8 | 0.83 | 50 | 71.3 | 40.2 | 69.4 | 40.8 | 220.2 | 214.5 | 214.5 | YES
10 | OK | 9 | 10 | 36 | 39 | 42.2 | 12.24 | 50 | 71.3 | 40.2 | 42.7 | 49.2 | 221.8 | 213.2 | 213.2 | YES
11 | OK | 16 | 17 | 17 | 47 | 100.8 | 2.92 | 50 | 71.3 | 40.2 | 64.4 | 40.2 | 220.4 | 214.6 | 214.6 | YES
12 | OK | 5 | 6 | 55 | 48 | 65.8 | 0.49 | 50 | 71.3 | 40.2 | 70.1 | 40.6 | 220 | 214.7 | 214.7 | YES
13 | OK | 10 | 12 | 36 | 39 | 42.2 | 11.98 | 50 | 71.3 | 40.2 | 43.3 | 49 | 221.8 | 213.2 | 213.2 | YES
14 | OK | 12 | 11 | 36 | 39 | 42.2 | 11.2 | 50 | 71.3 | 40.2 | 45.1 | 48.4 | 221.5 | 213.2 | 213.2 | YES
15 | OK | 11 | 35 | 36 | 39 | 42.2 | 9.66 | 50 | 71.3 | 40.2 | 48.7 | 47.3 | 220.8 | 213.1 | 213.1 | YES
16 | OK | 35 | 36 | 36 | 39 | 42.2 | 3.56 | 50 | 71.3 | 40.2 | 62.9 | 42.8 | 220.4 | 214.6 | 214.6 | YES
17 | OK | 35 | 30 | 29 | 43 | 43.1 | 5.96 | 50 | 71.3 | 40.2 | 57 | 44.7 | 220.6 | 211.1 | 211.1 | YES
18 | OK | 36 | 37 | 52 | 37 | 43 | 3.46 | 50 | 71.3 | 40.2 | 63.1 | 42.7 | 220.4 | 214.6 | 214.6 | YES
19 | OK | 30 | 29 | 29 | 43 | 43.1 | 4.47 | 50 | 71.3 | 40.2 | 60.9 | 43.6 | 219.1 | 211.3 | 211.3 | YES
20 | OK | 37 | 52 | 52 | 37 | 43 | 0.07 | 50 | 71.3 | 40.2 | 71.1 | 40.2 | 219.8 | 214.6 | 214.6 | YES
21 | OK | 29 | 28 | 28 | 45 | 43.3 | 1.59 | 50 | 71.3 | 40.2 | 67.6 | 41.4 | 219.6 | 213.6 | 213.6 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-004423
TR_B (available) | 63-022113
TR_A Rated kVA | 50
TR_B Rated kVA | 160
TR_A Baseline Loading% | 71.3
TR_B Baseline Loading% | 40.2
Total Scenarios Evaluated | 22
Feasible Scenarios | 21
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 33
Tie Node (TR_A side) | 17
Tie Node (TR_B side) | 47
Tie Line Distance (m) | 100.8
Load Transferred (kW) | 3.98
TR_A Loading After (%) | 62
TR_B Loading After (%) | 43.3
Minimum Voltage (V) | 215