## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 0 | 13 | 9 | 9 | 4.4 | 13.19 | 50 | 98.6 | 6.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 13 | 12 | 9 | 9 | 4.4 | 12.78 | 50 | 98.6 | 6.8 | 45.7 | 16.3 | 215.9 | 214.5 | 214.5 | YES
2 | ** OPTIMAL ** | 12 | 11 | 9 | 9 | 4.4 | 12.01 | 50 | 98.6 | 6.8 | 48.7 | 15.7 | 215.3 | 215.6 | 215.3 | YES
3 | OK | 11 | 10 | 9 | 9 | 4.4 | 10.85 | 50 | 98.6 | 6.8 | 53.1 | 14.8 | 214.4 | 217.2 | 214.4 | YES
4 | OK | 10 | 35 | 9 | 9 | 4.4 | 10.85 | 50 | 98.6 | 6.8 | 53.1 | 14.8 | 214.4 | 217.2 | 214.4 | YES
5 | OK | 35 | 36 | 9 | 9 | 4.4 | 10.26 | 50 | 98.6 | 6.8 | 55.4 | 14.4 | 214 | 218 | 214 | YES
6 | OK | 36 | 30 | 9 | 9 | 4.4 | 7.3 | 50 | 98.6 | 6.8 | 67.2 | 12.1 | 210 | 223.7 | 210 | YES
7 | OK | 30 | 23 | 9 | 9 | 4.4 | 7.3 | 50 | 98.6 | 6.8 | 67.2 | 12.1 | 210 | 223.7 | 210 | YES
| NG | 23 | 20 | 9 | 9 | 4.4 | 5.88 | 50 | 98.6 | 6.8 | 73 | 11 | 207.3 | 224.8 | 207.3 | NO
| NG | 20 | 22 | 9 | 9 | 4.4 | 5.8 | 50 | 98.6 | 6.8 | 73.3 | 11 | 207.1 | 224.8 | 207.1 | NO
| NG | 22 | 19 | 9 | 9 | 4.4 | 5.8 | 50 | 98.6 | 6.8 | 73.3 | 11 | 207.1 | 224.8 | 207.1 | NO
| NG | 19 | 18 | 9 | 9 | 4.4 | 5.8 | 50 | 98.6 | 6.8 | 73.3 | 11 | 207.1 | 224.8 | 207.1 | NO
| NG | 18 | 17 | 9 | 9 | 4.4 | 5.8 | 50 | 98.6 | 6.8 | 73.3 | 11 | 207.1 | 224.8 | 207.1 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 60-005788
TR_B (available) | 60-014049
TR_A Rated kVA | 30
TR_B Rated kVA | 160
TR_A Baseline Loading% | 98.6
TR_B Baseline Loading% | 6.8
Total Scenarios Evaluated | 13
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 12
Switch Child Node | 11
Tie Node (TR_A side) | 9
Tie Node (TR_B side) | 9
Tie Line Distance (m) | 4.4
Load Transferred (kW) | 12.01
TR_A Loading After (%) | 48.7
TR_B Loading After (%) | 15.7
Minimum Voltage (V) | 215.3