## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 49 | 37 | 65 | 20 | 81.4 | 15.31 | 50 | 79.8 | 18.4 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 37 | 36 | 65 | 20 | 81.4 | 14.03 | 50 | 79.8 | 18.4 | 24.5 | 55.6 | 224.4 | 187.6 | 187.6 | NO
| NG | 36 | 29 | 65 | 20 | 81.4 | 13.81 | 50 | 79.8 | 18.4 | 25.4 | 55.6 | 224.4 | 187.6 | 187.6 | NO
| NG | 29 | 14 | 65 | 20 | 81.4 | 13.81 | 50 | 79.8 | 18.4 | 25.4 | 55.6 | 224.4 | 187.6 | 187.6 | NO
| NG | 14 | 13 | 65 | 20 | 81.4 | 12.09 | 50 | 79.8 | 18.4 | 31.9 | 51.6 | 223.8 | 192.4 | 192.4 | NO
| NG | 13 | 9 | 65 | 20 | 81.4 | 12.09 | 50 | 79.8 | 18.4 | 31.9 |  | 223.8 | 5.0808e+58 | 223.8 | NO
| NG | 9 | 10 | 65 | 20 | 81.4 | 5.86 | 50 | 79.8 | 18.4 | 56.2 | 42.3 | 219.4 | 207.4 | 207.4 | NO
| NG | 10 | 12 | 65 | 20 | 81.4 | 5.76 | 50 | 79.8 | 18.4 | 56.6 | 41.9 | 219.4 | 207.9 | 207.9 | NO
1 | OK | 12 | 68 | 65 | 20 | 81.4 | 4.06 | 50 | 79.8 | 18.4 | 63.2 | 34.5 | 218.4 | 216 | 216 | YES
2 | OK | 68 | 54 | 65 | 20 | 81.4 | 3.84 | 50 | 79.8 | 18.4 | 64.1 | 33.6 | 218.1 | 216.9 | 216.9 | YES
3 | OK | 54 | 55 | 65 | 20 | 81.4 | 3.84 | 50 | 79.8 | 18.4 | 64.1 | 33.6 | 218.1 | 216.9 | 216.9 | YES
4 | ** OPTIMAL ** | 55 | 70 | 65 | 20 | 81.4 | 3.43 | 50 | 79.8 | 18.4 | 65.7 | 31.9 | 217.5 | 218.5 | 217.5 | YES
5 | OK | 70 | 57 | 65 | 20 | 81.4 | 3.15 | 50 | 79.8 | 18.4 | 66.8 | 30.8 | 217 | 219.6 | 217 | YES
6 | OK | 57 | 58 | 65 | 20 | 81.4 | 2.84 | 50 | 79.8 | 18.4 | 68 | 29.5 | 216.6 | 220.6 | 216.6 | YES
7 | OK | 58 | 69 | 65 | 20 | 81.4 | 2.84 | 50 | 79.8 | 18.4 | 68 | 29.5 | 216.6 | 220.6 | 216.6 | YES
8 | OK | 69 | 62 | 65 | 20 | 81.4 | 2.04 | 50 | 79.8 | 18.4 | 71.2 | 26.3 | 215.3 | 223.2 | 215.3 | YES
9 | OK | 62 | 63 | 65 | 20 | 81.4 | 1.93 | 50 | 79.8 | 18.4 | 71.7 | 25.9 | 215.1 | 223.5 | 215.1 | YES
10 | OK | 63 | 59 | 65 | 20 | 81.4 | 1.71 | 50 | 79.8 | 18.4 | 72.6 | 25 | 214.8 | 224.1 | 214.8 | YES
11 | OK | 59 | 60 | 65 | 20 | 81.4 | 1.71 | 50 | 79.8 | 18.4 | 72.6 | 25 | 214.8 | 224.1 | 214.8 | YES
12 | OK | 60 | 64 | 65 | 20 | 81.4 | 1.55 | 50 | 79.8 | 18.4 | 73.2 | 24.4 | 214.5 | 224.4 | 214.5 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-007045
TR_B (available) | 30-005507
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79.8
TR_B Baseline Loading% | 18.4
Total Scenarios Evaluated | 20
Feasible Scenarios | 12
--- Optimal Solution ---
Switch Parent Node | 55
Switch Child Node | 70
Tie Node (TR_A side) | 65
Tie Node (TR_B side) | 20
Tie Line Distance (m) | 81.4
Load Transferred (kW) | 3.43
TR_A Loading After (%) | 65.7
TR_B Loading After (%) | 31.9
Minimum Voltage (V) | 217.5