## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 49 | 50 | 30 | 30 | 4.1 | 5.1 | 50 | 79.8 | 39.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 50 | 44 | 30 | 30 | 4.1 | 4.23 | 50 | 79.8 | 39.8 | 63.4 | 50.4 | 211.4 | 219.4 | 211.4 | YES
2 | OK | 44 | 45 | 30 | 30 | 4.1 | 4.05 | 50 | 79.8 | 39.8 | 64.1 | 50.4 | 211.3 | 219.4 | 211.3 | YES
3 | OK | 45 | 51 | 30 | 30 | 4.1 | 3.46 | 50 | 79.8 | 39.8 | 66.3 | 50.4 | 211.3 | 219.4 | 211.3 | YES
4 | OK | 51 | 39 | 30 | 30 | 4.1 | 3.46 | 50 | 79.8 | 39.8 | 66.3 | 50.4 | 211.3 | 219.4 | 211.3 | YES
5 | OK | 14 | 28 | 28 | 33 | 19.3 | 1.72 | 50 | 79.8 | 39.8 | 73 | 42.7 | 210.1 | 222.8 | 210.1 | YES
6 | OK | 39 | 30 | 30 | 30 | 4.1 | 3.46 | 50 | 79.8 | 39.8 | 66.3 | 50.4 | 211.3 | 219.4 | 211.3 | YES
7 | OK | 28 | 53 | 53 | 33 | 25.8 | 1.72 | 50 | 79.8 | 39.8 | 73 | 42.7 | 210.1 | 222.8 | 210.1 | YES
8 | OK | 30 | 31 | 31 | 31 | 8.7 | 3.25 | 50 | 79.8 | 39.8 | 67.1 | 49.5 | 211.1 | 219.8 | 211.1 | YES
| NG | 30 | 40 | 17 | 32 | 4.7 | 0.21 | 50 | 79.8 | 39.8 | 78.9 | 40.6 | 209.3 | 222.8 | 209.3 | NO
9 | OK | 9 | 10 | 54 | 38 | 7.1 | 5.86 | 50 | 79.8 | 39.8 | 56.2 | 63.2 | 219.4 | 210.4 | 210.4 | YES
10 | OK | 9 | 6 | 11 | 34 | 3.4 | 5.28 | 50 | 79.8 | 39.8 | 58.9 | 47.3 | 212.1 | 220.7 | 212.1 | YES
11 | OK | 53 | 67 | 67 | 33 | 55.3 | 1.66 | 50 | 79.8 | 39.8 | 73.2 | 42.7 | 210.1 | 222.8 | 210.1 | YES
12 | OK | 31 | 61 | 61 | 31 | 22.1 | 3.09 | 50 | 79.8 | 39.8 | 67.8 | 49.5 | 211.1 | 220 | 211.1 | YES
| NG | 40 | 16 | 17 | 32 | 4.7 | 0.21 | 50 | 79.8 | 39.8 | 78.9 | 40.6 | 209.3 | 222.8 | 209.3 | NO
13 | OK | 10 | 12 | 54 | 38 | 7.1 | 5.76 | 50 | 79.8 | 39.8 | 56.6 | 62.8 | 219.4 | 210.7 | 210.7 | YES
14 | OK | 6 | 4 | 11 | 34 | 3.4 | 4.48 | 50 | 79.8 | 39.8 | 61.9 | 47.3 | 212.1 | 220.7 | 212.1 | YES
15 | OK | 67 | 27 | 66 | 43 | 60.6 | 0.77 | 50 | 79.8 | 39.8 | 76.7 | 42.8 | 210.2 | 222.9 | 210.2 | YES
16 | OK | 61 | 18 | 24 | 42 | 37.6 | 3.09 | 50 | 79.8 | 39.8 | 67.8 | 49.7 | 211.1 | 215.7 | 211.1 | YES
17 | OK | 12 | 68 | 54 | 38 | 7.1 | 4.06 | 50 | 79.8 | 39.8 | 63.2 | 55.9 | 218.4 | 214.5 | 214.5 | YES
18 | OK | 4 | 5 | 11 | 34 | 3.4 | 2.38 | 50 | 79.8 | 39.8 | 70.1 | 47 | 212.1 | 220.9 | 212.1 | YES
19 | OK | 27 | 26 | 66 | 43 | 60.6 | 0.77 | 50 | 79.8 | 39.8 | 76.7 | 41.3 | 210.2 | 222.8 | 210.2 | YES
20 | OK | 18 | 19 | 24 | 42 | 37.6 | 2.62 | 50 | 79.8 | 39.8 | 69.6 | 48.7 | 210.9 | 217 | 210.9 | YES
21 | OK | 68 | 54 | 54 | 38 | 7.1 | 3.84 | 50 | 79.8 | 39.8 | 64.1 | 55 | 218.1 | 215 | 215 | YES
22 | OK | 5 | 11 | 11 | 34 | 3.4 | 2.38 | 50 | 79.8 | 39.8 | 70.1 | 47 | 212.1 | 220.9 | 212.1 | YES
| NG | 26 | 52 | 66 | 43 | 60.6 | 0.38 | 50 | 79.8 | 39.8 | 78.2 | 41.3 | 209.6 | 222.8 | 209.6 | NO
23 | OK | 19 | 20 | 24 | 42 | 37.6 | 2.62 | 50 | 79.8 | 39.8 | 69.6 | 48.7 | 210.9 | 217 | 210.9 | YES
24 | OK | 54 | 55 | 55 | 38 | 44.7 | 3.84 | 50 | 79.8 | 39.8 | 64.1 | 55 | 218.1 | 215 | 215 | YES
25 | OK | 11 | 0 | 35 | 42 | 3.5 | 1.7 | 50 | 79.8 | 39.8 | 72.8 | 46.4 | 211.9 | 220.7 | 211.9 | YES
| NG | 11 | 47 | 3 | 35 | 24.2 | 0.68 | 50 | 79.8 | 39.8 | 77.1 | 40.4 | 209.3 | 222.8 | 209.3 | NO
| NG | 52 | 66 | 66 | 43 | 60.6 | 0.11 | 50 | 79.8 | 39.8 | 79.3 | 40.2 | 209.2 | 222.8 | 209.2 | NO
26 | OK | 20 | 21 | 24 | 42 | 37.6 | 2.13 | 50 | 79.8 | 39.8 | 71.4 | 46.7 | 210.5 | 219.3 | 210.5 | YES
27 | OK | 55 | 70 | 70 | 38 | 61.4 | 3.43 | 50 | 79.8 | 39.8 | 65.7 | 53.3 | 217.5 | 216 | 216 | YES
28 | OK | 0 | 1 | 35 | 42 | 3.5 | 1.7 | 50 | 79.8 | 39.8 | 72.8 | 46.4 | 211.9 | 220.7 | 211.9 | YES
| NG | 47 | 48 | 3 | 35 | 24.2 | 0.68 | 50 | 79.8 | 39.8 | 77.1 | 40.4 | 209.3 | 222.8 | 209.3 | NO
| NG | 66 | 41 | 41 | 43 | 88.9 | 0.11 | 50 | 79.8 | 39.8 | 79.3 | 40.2 | 209.2 | 222.8 | 209.2 | NO
| NG | 21 | 22 | 24 | 42 | 37.6 | 0.6 | 50 | 79.8 | 39.8 | 77.4 | 40.7 | 209.3 | 222.8 | 209.3 | NO
29 | OK | 70 | 57 | 58 | 27 | 73.4 | 3.15 | 50 | 79.8 | 39.8 | 66.8 | 52.3 | 217 | 216.1 | 216.1 | YES
30 | OK | 1 | 38 | 35 | 42 | 3.5 | 1.7 | 50 | 79.8 | 39.8 | 72.8 | 46.4 | 211.9 | 220.7 | 211.9 | YES
| NG | 48 | 2 | 3 | 35 | 24.2 | 0.51 | 50 | 79.8 | 39.8 | 77.7 | 40.1 | 209.2 | 222.8 | 209.2 | NO
| NG | 22 | 23 | 24 | 42 | 37.6 | 0.48 | 50 | 79.8 | 39.8 | 77.9 | 40.7 | 209.3 | 222.8 | 209.3 | NO
31 | OK | 57 | 58 | 58 | 27 | 73.4 | 2.84 | 50 | 79.8 | 39.8 | 68 | 51.1 | 216.6 | 216.9 | 216.6 | YES
32 | OK | 38 | 32 | 35 | 42 | 3.5 | 1.5 | 50 | 79.8 | 39.8 | 73.6 | 45.6 | 211.6 | 221.6 | 211.6 | YES
| NG | 2 | 3 | 3 | 35 | 24.2 | 0.42 | 50 | 79.8 | 39.8 | 78.1 | 39.8 | 209.1 | 222.8 | 209.1 | NO
33 | ** OPTIMAL ** | 58 | 69 | 69 | 27 | 82.1 | 2.84 | 50 | 79.8 | 39.8 | 68 | 51.1 | 216.6 | 217.4 | 216.6 | YES
34 | OK | 32 | 33 | 35 | 42 | 3.5 | 0.98 | 50 | 79.8 | 39.8 | 75.7 | 43.6 | 210.7 | 222.8 | 210.7 | YES
| NG | 3 | 15 | 15 | 35 | 73.6 | 0.42 | 50 | 79.8 | 39.8 | 78.1 | 41.4 | 209.1 | 222.8 | 209.1 | NO
35 | OK | 69 | 62 | 62 | 27 | 107.2 | 2.04 | 50 | 79.8 | 39.8 | 71.2 | 47.8 | 215.3 | 219.4 | 215.3 | YES
36 | OK | 33 | 34 | 35 | 42 | 3.5 | 0.59 | 50 | 79.8 | 39.8 | 77.3 | 42.1 | 210.1 | 222.8 | 210.1 | YES
| NG | 15 | 56 | 56 | 35 | 108.7 | 0.42 | 50 | 79.8 | 39.8 | 78.1 | 41.4 | 209.1 | 222.8 | 209.1 | NO
37 | OK | 62 | 63 | 63 | 27 | 139.4 | 1.93 | 50 | 79.8 | 39.8 | 71.7 | 47.4 | 215.1 | 219.7 | 215.1 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-007045
TR_B (available) | 58-005488
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79.8
TR_B Baseline Loading% | 39.8
Total Scenarios Evaluated | 51
Feasible Scenarios | 37
--- Optimal Solution ---
Switch Parent Node | 58
Switch Child Node | 69
Tie Node (TR_A side) | 69
Tie Node (TR_B side) | 27
Tie Line Distance (m) | 82.1
Load Transferred (kW) | 2.84
TR_A Loading After (%) | 68
TR_B Loading After (%) | 51.1
Minimum Voltage (V) | 216.6