## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 14 | 28 | 43 | 4 | 57.1 | 1.72 | 50 | 79.8 | 40 | 73 | 43 | 210.1 | 217.6 | 210.1 | YES
2 | OK | 28 | 53 | 43 | 4 | 57.1 | 1.72 | 50 | 79.8 | 40 | 73 | 43 | 210.1 | 217.6 | 210.1 | YES
3 | OK | 53 | 67 | 43 | 4 | 57.1 | 1.66 | 50 | 79.8 | 40 | 73.2 | 43 | 210.1 | 217.6 | 210.1 | YES
4 | OK | 67 | 27 | 43 | 4 | 57.1 | 0.77 | 50 | 79.8 | 40 | 76.7 | 43 | 210.2 | 217.6 | 210.2 | YES
5 | ** OPTIMAL ** | 27 | 26 | 43 | 4 | 57.1 | 0.77 | 50 | 79.8 | 40 | 76.7 | 41.5 | 210.2 | 217.9 | 210.2 | YES
| NG | 26 | 52 | 43 | 4 | 57.1 | 0.38 | 50 | 79.8 | 40 | 78.2 | 41.5 | 209.6 | 217.9 | 209.6 | NO
| NG | 52 | 66 | 43 | 4 | 57.1 | 0.11 | 50 | 79.8 | 40 | 79.3 | 40.4 | 209.2 | 218.1 | 209.2 | NO
| NG | 66 | 41 | 43 | 4 | 57.1 | 0.11 | 50 | 79.8 | 40 | 79.3 | 40.4 | 209.2 | 218.1 | 209.2 | NO

## Summary
Parameter | Value
TR_A (overloaded) | 60-007045
TR_B (available) | 59-003747
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 79.8
TR_B Baseline Loading% | 40
Total Scenarios Evaluated | 8
Feasible Scenarios | 5
--- Optimal Solution ---
Switch Parent Node | 27
Switch Child Node | 26
Tie Node (TR_A side) | 43
Tie Node (TR_B side) | 4
Tie Line Distance (m) | 57.1
Load Transferred (kW) | 0.77
TR_A Loading After (%) | 76.7
TR_B Loading After (%) | 41.5
Minimum Voltage (V) | 210.2