## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 18 | 42 | 13 | 3 | 188.8 | 9.08 | 50 | 79.1 | 42.3 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 42 | 43 | 13 | 3 | 188.8 | 9.08 | 50 | 79.1 | 42.3 | [5 empty] | NO | TR_B sim: not converged
| NG | 43 | 36 | 13 | 3 | 188.8 | 9.08 | 50 | 79.1 | 42.3 | [5 empty] | NO | TR_B sim: not converged
| NG | 36 | 37 | 13 | 3 | 188.8 | 3.09 | 50 | 79.1 | 42.3 | 66.6 | 50.3 | 212.9 | 200.7 | 200.7 | NO
| NG | 36 | 31 | 19 | 36 | 225.9 | 5 | 50 | 79.1 | 42.3 | 54.9 | 54.8 | 212.9 | 205.3 | 205.3 | NO
| NG | 37 | 15 | 13 | 3 | 188.8 | 2.4 | 50 | 79.1 | 42.3 | 69.3 | 48.4 | 212.9 | 205 | 205 | NO
| NG | 31 | 32 | 19 | 36 | 225.9 | 5 | 50 | 79.1 | 42.3 | 58.7 | 54.8 | 212.9 | 205.3 | 205.3 | NO
| NG | 15 | 16 | 13 | 3 | 188.8 | 2.32 | 50 | 79.1 | 42.3 | 69.6 | 48.2 | 212.9 | 205.5 | 205.5 | NO
| NG | 32 | 44 | 19 | 36 | 225.9 | 5 | 50 | 79.1 | 42.3 | 58.7 | 54.8 | 212.9 | 205.3 | 205.3 | NO
| NG | 16 | 46 | 13 | 3 | 188.8 | 2.32 | 50 | 79.1 | 42.3 | 69.6 | 48.2 | 212.9 | 205.5 | 205.5 | NO
| NG | 44 | 45 | 19 | 36 | 225.9 | 5 | 50 | 79.1 | 42.3 | 58.7 | 54.8 | 212.9 | 205.3 | 205.3 | NO
| NG | 46 | 11 | 13 | 3 | 188.8 | 2.32 | 50 | 79.1 | 42.3 | 69.6 | 48.2 | 212.9 | 205.5 | 205.5 | NO
| NG | 45 | 29 | 19 | 36 | 225.9 | 4.76 | 50 | 79.1 | 42.3 | 59.6 | 54.1 | 212.9 | 206.4 | 206.4 | NO
1 | OK | 11 | 33 | 13 | 3 | 188.8 | 0.68 | 50 | 79.1 | 42.3 | 76.3 | 43.9 | 212.2 | 217.2 | 212.2 | YES
| NG | 29 | 30 | 19 | 36 | 225.9 | 4.06 | 50 | 79.1 | 42.3 | 62.4 | 52.2 | 212.9 | 209.3 | 209.3 | NO
2 | OK | 33 | 13 | 13 | 3 | 188.8 | 0.68 | 50 | 79.1 | 42.3 | 76.3 | 43.9 | 212.2 | 217.2 | 212.2 | YES
3 | OK | 30 | 39 | 19 | 36 | 225.9 | 1.42 | 50 | 79.1 | 42.3 | 73 | 45.6 | 212.9 | 219.1 | 212.9 | YES
4 | OK | 13 | 14 | 14 | 3 | 191.1 | 0.68 | 50 | 79.1 | 42.3 | 76.3 | 42.3 | 212.2 | 219.8 | 212.2 | YES
5 | OK | 39 | 40 | 19 | 36 | 225.9 | 1.37 | 50 | 79.1 | 42.3 | 73.3 | 45.5 | 212.9 | 219.1 | 212.9 | YES
6 | OK | 40 | 20 | 19 | 36 | 225.9 | 1.13 | 50 | 79.1 | 42.3 | 74.3 | 44.9 | 212.9 | 219.2 | 212.9 | YES
7 | ** OPTIMAL ** | 20 | 19 | 19 | 36 | 225.9 | 0.8 | 50 | 79.1 | 42.3 | 75.6 | 44.1 | 212.9 | 219.4 | 212.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-007689
TR_B (available) | 60-011941
TR_A Rated kVA | 30
TR_B Rated kVA | 50
TR_A Baseline Loading% | 79.1
TR_B Baseline Loading% | 42.3
Total Scenarios Evaluated | 21
Feasible Scenarios | 7
--- Optimal Solution ---
Switch Parent Node | 20
Switch Child Node | 19
Tie Node (TR_A side) | 19
Tie Node (TR_B side) | 36
Tie Line Distance (m) | 225.9
Load Transferred (kW) | 0.8
TR_A Loading After (%) | 75.6
TR_B Loading After (%) | 44.1
Minimum Voltage (V) | 212.9