## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 4 | 5 | 5 | 36 | 8.1 | 8.23 | 50 | 90.7 | 45.2 | 57.6 | 72.5 | 218.3 | 212.6 | 212.6 | YES
2 | OK | 5 | 24 | 24 | 36 | 11.5 | 7.9 | 50 | 90.7 | 45.2 | 58.9 | 71.2 | 218.3 | 213.3 | 213.3 | YES
3 | OK | 24 | 25 | 25 | 36 | 31.1 | 7.9 | 50 | 90.7 | 45.2 | 58.9 | 71.2 | 218.3 | 213.3 | 213.3 | YES
4 | OK | 25 | 11 | 11 | 36 | 37.9 | 7.74 | 50 | 90.7 | 45.2 | 59.5 | 70.5 | 218.2 | 213.6 | 213.6 | YES
5 | OK | 11 | 2 | 12 | 36 | 69.6 | 7.74 | 50 | 90.7 | 45.2 | 59.5 | 70.5 | 218.2 | 213.6 | 213.6 | YES
6 | OK | 31 | 42 | 33 | 16 | 102.5 | 8.72 | 50 | 90.7 | 45.2 | 55 | 61.4 | 218.9 | 213.9 | 213.9 | YES
7 | ** OPTIMAL ** | 2 | 12 | 12 | 36 | 69.6 | 5.14 | 50 | 90.7 | 45.2 | 69.5 | 63.7 | 217 | 216.6 | 216.6 | YES
8 | OK | 42 | 37 | 33 | 16 | 102.5 | 8.72 | 50 | 90.7 | 45.2 | 55 | 61.4 | 218.9 | 213.9 | 213.9 | YES
9 | OK | 12 | 15 | 15 | 36 | 78.2 | 4.7 | 50 | 90.7 | 45.2 | 71.2 | 61.9 | 216.6 | 217.7 | 216.6 | YES
10 | OK | 37 | 36 | 33 | 16 | 102.5 | 7.96 | 50 | 90.7 | 45.2 | 57.9 | 61.4 | 218.9 | 213.9 | 213.9 | YES
11 | OK | 15 | 40 | 40 | 36 | 79.2 | 4.7 | 50 | 90.7 | 45.2 | 71.2 | 61.9 | 216.6 | 217.8 | 216.6 | YES
12 | OK | 36 | 23 | 33 | 16 | 102.5 | 7.57 | 50 | 90.7 | 45.2 | 59.4 | 61.4 | 218.9 | 213.9 | 213.9 | YES
13 | OK | 40 | 47 | 47 | 36 | 120.5 | 3.88 | 50 | 90.7 | 45.2 | 74.3 | 58.7 | 216 | 219.4 | 216 | YES
14 | OK | 23 | 22 | 33 | 16 | 102.5 | 6.99 | 50 | 90.7 | 45.2 | 61.7 | 61.4 | 218.9 | 213.9 | 213.9 | YES
15 | OK | 22 | 49 | 33 | 16 | 102.5 | 6.68 | 50 | 90.7 | 45.2 | 61.7 | 61.4 | 218.9 | 213.9 | 213.9 | YES
16 | OK | 49 | 50 | 50 | 16 | 165.7 | 4.4 | 50 | 90.7 | 45.2 | 70.6 | 62.5 | 216.4 | 218.1 | 216.4 | YES
17 | OK | 50 | 48 | 48 | 16 | 171 | 4.4 | 50 | 90.7 | 45.2 | 71.8 | 62.5 | 216.5 | 218.1 | 216.5 | YES
18 | OK | 48 | 44 | 46 | 16 | 199.5 | 4.4 | 50 | 90.7 | 45.2 | 71.8 | 52.2 | 216.5 | 220.3 | 216.5 | YES
19 | OK | 44 | 17 | 17 | 16 | 213.8 | 3.97 | 50 | 90.7 | 45.2 | 73.5 | 60.8 | 215.7 | 218.1 | 215.7 | YES
20 | OK | 17 | 16 | 16 | 16 | 252.2 | 3.6 | 50 | 90.7 | 45.2 | 74.9 | 59.4 | 215 | 218.1 | 215 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-008536
TR_B (available) | 55-000560
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 90.7
TR_B Baseline Loading% | 45.2
Total Scenarios Evaluated | 20
Feasible Scenarios | 20
--- Optimal Solution ---
Switch Parent Node | 2
Switch Child Node | 12
Tie Node (TR_A side) | 12
Tie Node (TR_B side) | 36
Tie Line Distance (m) | 69.6
Load Transferred (kW) | 5.14
TR_A Loading After (%) | 69.5
TR_B Loading After (%) | 63.7
Minimum Voltage (V) | 216.6