## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
1 | OK | 2 | 12 | 12 | 37 | 62.2 | 5.14 | 50 | 90.7 | 57.1 | 69.5 | 75.5 | 217 | 215.1 | 215.1 | YES
2 | OK | 12 | 15 | 15 | 37 | 75.8 | 4.7 | 50 | 90.7 | 57.1 | 71.2 | 73.7 | 216.6 | 216.1 | 216.1 | YES
3 | ** OPTIMAL ** | 15 | 40 | 40 | 37 | 77.1 | 4.7 | 50 | 90.7 | 57.1 | 71.2 | 73.7 | 216.6 | 216.2 | 216.2 | YES
4 | OK | 40 | 47 | 47 | 17 | 121.6 | 3.88 | 50 | 90.7 | 57.1 | 74.3 | 72.3 | 216 | 214.9 | 214.9 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-008536
TR_B (available) | 66-015605
TR_A Rated kVA | 30
TR_B Rated kVA | 30
TR_A Baseline Loading% | 90.7
TR_B Baseline Loading% | 57.1
Total Scenarios Evaluated | 4
Feasible Scenarios | 4
--- Optimal Solution ---
Switch Parent Node | 15
Switch Child Node | 40
Tie Node (TR_A side) | 40
Tie Node (TR_B side) | 37
Tie Line Distance (m) | 77.1
Load Transferred (kW) | 4.7
TR_A Loading After (%) | 71.2
TR_B Loading After (%) | 73.7
Minimum Voltage (V) | 216.2