## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 7 | 12 | 6 | 91.6 | 17.82 | 50 | 68.7 | 30.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 50 | 43 | 2 | 7 | 59.4 | 11.86 | 50 | 68.7 | 30.1 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 7 | 6 | 12 | 6 | 91.6 | 17.82 | 50 | 68.7 | 30.1 | 27.5 | 73.2 | 222.8 | 205.6 | 205.6 | NO
1 | OK | 43 | 44 | 2 | 7 | 59.4 | 11.86 | 50 | 68.7 | 30.1 | 41.2 | 57.8 | 221.1 | 217.9 | 217.9 | YES
2 | OK | 6 | 4 | 12 | 6 | 91.6 | 7.02 | 50 | 68.7 | 30.1 | 52.4 | 46.7 | 220.2 | 216.1 | 216.1 | YES
3 | OK | 6 | 65 | 24 | 18 | 125.9 | 0.17 | 50 | 68.7 | 30.1 | 68.3 | 30.5 | 218.1 | 224.9 | 218.1 | YES
4 | OK | 44 | 13 | 2 | 7 | 59.4 | 11.82 | 50 | 68.7 | 30.1 | 41.3 | 57.7 | 221.1 | 218 | 218 | YES
5 | OK | 4 | 5 | 12 | 6 | 91.6 | 1.64 | 50 | 68.7 | 30.1 | 64.9 | 33.9 | 218.6 | 224.1 | 218.6 | YES
6 | OK | 65 | 22 | 24 | 18 | 125.9 | 0.17 | 50 | 68.7 | 30.1 | 68.3 | 30.5 | 218.1 | 224.9 | 218.1 | YES
7 | OK | 13 | 2 | 2 | 7 | 59.4 | 11.51 | 50 | 68.7 | 30.1 | 42 | 57 | 221.1 | 218 | 218 | YES
8 | OK | 5 | 9 | 12 | 6 | 91.6 | 1.4 | 50 | 68.7 | 30.1 | 65.5 | 33.4 | 218.6 | 224.1 | 218.6 | YES
9 | OK | 22 | 23 | 24 | 18 | 125.9 | 0.17 | 50 | 68.7 | 30.1 | 68.3 | 30.5 | 218.1 | 224.9 | 218.1 | YES
10 | OK | 2 | 3 | 28 | 2 | 63.7 | 1.17 | 50 | 68.7 | 30.1 | 66 | 32.8 | 218 | 224.9 | 218 | YES
11 | OK | 2 | 14 | 15 | 6 | 60.8 | 9.67 | 50 | 68.7 | 30.1 | 46.2 | 52.8 | 221.1 | 217.1 | 217.1 | YES
12 | OK | 9 | 10 | 12 | 6 | 91.6 | 0.48 | 50 | 68.7 | 30.1 | 67.6 | 31.2 | 218.1 | 224.9 | 218.1 | YES
13 | OK | 3 | 25 | 28 | 2 | 63.7 | 0.51 | 50 | 68.7 | 30.1 | 67.5 | 31.3 | 218.1 | 224.9 | 218.1 | YES
14 | OK | 14 | 15 | 15 | 6 | 60.8 | 9.67 | 50 | 68.7 | 30.1 | 46.2 | 52.8 | 221.1 | 217.1 | 217.1 | YES
15 | OK | 10 | 11 | 12 | 6 | 91.6 | 0.48 | 50 | 68.7 | 30.1 | 67.6 | 31.2 | 218.1 | 224.9 | 218.1 | YES
16 | OK | 25 | 26 | 28 | 2 | 63.7 | 0.21 | 50 | 68.7 | 30.1 | 68.2 | 30.6 | 218.1 | 224.9 | 218.1 | YES
17 | OK | 15 | 16 | 16 | 1 | 62.6 | 9.02 | 50 | 68.7 | 30.1 | 47.7 | 51.3 | 221.1 | 217.2 | 217.2 | YES
18 | OK | 11 | 12 | 12 | 6 | 91.6 | 0.04 | 50 | 68.7 | 30.1 | 68.6 | 30.2 | 218.1 | 224.9 | 218.1 | YES
19 | OK | 26 | 27 | 28 | 2 | 63.7 | 0.21 | 50 | 68.7 | 30.1 | 68.2 | 30.6 | 218.1 | 224.9 | 218.1 | YES
20 | OK | 16 | 17 | 17 | 0 | 64.4 | 8.75 | 50 | 68.7 | 30.1 | 48.3 | 50.7 | 221 | 217.7 | 217.7 | YES
21 | OK | 27 | 28 | 28 | 2 | 63.7 | 0.21 | 50 | 68.7 | 30.1 | 68.2 | 30.6 | 218.1 | 224.9 | 218.1 | YES
22 | OK | 17 | 39 | 39 | 13 | 64.5 | 7.32 | 50 | 68.7 | 30.1 | 51.6 | 47.3 | 220.8 | 218 | 218 | YES
23 | OK | 39 | 18 | 18 | 13 | 65.3 | 7.15 | 50 | 68.7 | 30.1 | 52 | 43.2 | 220.8 | 217.9 | 217.9 | YES
24 | OK | 18 | 19 | 19 | 13 | 72.6 | 5.54 | 50 | 68.7 | 30.1 | 55.4 | 43.2 | 220.8 | 217.9 | 217.9 | YES
25 | ** OPTIMAL ** | 19 | 45 | 45 | 13 | 113.8 | 4.75 | 50 | 68.7 | 30.1 | 57.6 | 41.3 | 220.4 | 219.4 | 219.4 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-012497
TR_B (available) | 26-011420
TR_A Rated kVA | 50
TR_B Rated kVA | 50
TR_A Baseline Loading% | 68.7
TR_B Baseline Loading% | 30.1
Total Scenarios Evaluated | 28
Feasible Scenarios | 25
--- Optimal Solution ---
Switch Parent Node | 19
Switch Child Node | 45
Tie Node (TR_A side) | 45
Tie Node (TR_B side) | 13
Tie Line Distance (m) | 113.8
Load Transferred (kW) | 4.75
TR_A Loading After (%) | 57.6
TR_B Loading After (%) | 41.3
Minimum Voltage (V) | 219.4