## Results
Rank | Status | Switch_Parent_Node | Switch_Child_Node | TieNode_A | TieNode_B | TieDistance_m | TransferredLoad_kW | TieConductorSize_mm2 | TRA_Loading_Before% | TRB_Loading_Before% | TRA_Loading_After% | TRB_Loading_After% | TRA_MinVolt_V | TRB_MinVolt_V | Overall_MinVolt_V | Feasible | Error
| NG | 50 | 49 | 30 | 6 | 41.6 | 35.66 | 50 | 57.4 | 19.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
| NG | 50 | 21 | 66 | 43 | 39.6 | 37.84 | 50 | 57.4 | 19.8 | [5 empty] | NO | TR_A sim: source มีสาย LC ออกน้อยกว่า 2 เส้น จึงแบ่ง Feeder1/Feeder2 ไม่ได้
1 | OK | 49 | 20 | 30 | 6 | 41.6 | 35.66 | 50 | 57.4 | 19.8 | 31.4 | 36.4 | 221 | 221.1 | 221 | YES
| NG | 21 | 22 | 66 | 43 | 39.6 | 37.8 | 50 | 57.4 | 19.8 | 29.9 | 38.7 | 221.9 | 201.7 | 201.7 | NO
2 | OK | 20 | 19 | 30 | 6 | 41.6 | 35.48 | 50 | 57.4 | 19.8 | 31.6 | 36.4 | 221 | 221 | 221 | YES
| NG | 22 | 43 | 66 | 43 | 39.6 | 37.8 | 50 | 57.4 | 19.8 | 29.9 | 38.7 | 221.9 | 201.7 | 201.7 | NO
3 | OK | 19 | 63 | 30 | 6 | 41.6 | 35.48 | 50 | 57.4 | 19.8 | 31.6 | 36.4 | 221 | 221 | 221 | YES
4 | OK | 43 | 17 | 17 | 14 | 63.9 | 6.21 | 50 | 57.4 | 19.8 | 52.9 | 22.7 | 220.3 | 222.7 | 220.3 | YES
5 | OK | 43 | 69 | 66 | 43 | 39.6 | 30.58 | 50 | 57.4 | 19.8 | 34.3 | 34.8 | 221.8 | 210.5 | 210.5 | YES
6 | OK | 63 | 48 | 30 | 6 | 41.6 | 35.41 | 50 | 57.4 | 19.8 | 31.6 | 36.3 | 221 | 221 | 221 | YES
7 | OK | 17 | 18 | 18 | 14 | 85.8 | 6.21 | 50 | 57.4 | 19.8 | 52.9 | 22.7 | 220.3 | 222.7 | 220.3 | YES
| NG | 69 | 23 | 66 | 43 | 39.6 | 30.58 | 50 | 57.4 | 19.8 | [5 empty] | NO | TR_B sim: loading 0.0% despite baseline 19.8% (degenerate)
8 | OK | 48 | 16 | 30 | 6 | 41.6 | 35.41 | 50 | 57.4 | 19.8 | 31.6 | 34.6 | 221 | 220.6 | 220.6 | YES
9 | OK | 18 | 14 | 14 | 15 | 105.9 | 4.45 | 50 | 57.4 | 19.8 | 54.2 | 21.8 | 220.3 | 222.7 | 220.3 | YES
10 | OK | 23 | 24 | 66 | 43 | 39.6 | 29.67 | 50 | 57.4 | 19.8 | 35.7 | 34.3 | 221.8 | 212.4 | 212.4 | YES
11 | OK | 16 | 37 | 30 | 6 | 41.6 | 28.31 | 50 | 57.4 | 19.8 | 36.7 | 32.9 | 220.6 | 222.5 | 220.6 | YES
12 | OK | 14 | 15 | 15 | 15 | 145.2 | 4.03 | 50 | 57.4 | 19.8 | 54.5 | 21.6 | 220.2 | 222.8 | 220.2 | YES
13 | OK | 24 | 64 | 66 | 43 | 39.6 | 22 | 50 | 57.4 | 19.8 | 41.2 | 30.5 | 221.4 | 213.5 | 213.5 | YES
14 | OK | 37 | 36 | 30 | 6 | 41.6 | 24.02 | 50 | 57.4 | 19.8 | 38.8 | 30.9 | 220.6 | 222.6 | 220.6 | YES
15 | OK | 64 | 73 | 66 | 43 | 39.6 | 21.26 | 50 | 57.4 | 19.8 | 41.8 | 28.7 | 221.3 | 217 | 217 | YES
16 | OK | 36 | 35 | 30 | 6 | 41.6 | 22.45 | 50 | 57.4 | 19.8 | 40.9 | 30.2 | 220.4 | 222.6 | 220.4 | YES
17 | OK | 73 | 72 | 66 | 43 | 39.6 | 18.51 | 50 | 57.4 | 19.8 | 43.7 | 28.7 | 221.3 | 217 | 217 | YES
18 | OK | 35 | 52 | 30 | 6 | 41.6 | 22.45 | 50 | 57.4 | 19.8 | 40.9 | 30.2 | 220.4 | 222.6 | 220.4 | YES
19 | OK | 72 | 65 | 66 | 43 | 39.6 | 18.51 | 50 | 57.4 | 19.8 | 43.7 | 28.7 | 221.3 | 217 | 217 | YES
20 | OK | 52 | 70 | 30 | 6 | 41.6 | 22.18 | 50 | 57.4 | 19.8 | 41.1 | 30.1 | 220.4 | 222.6 | 220.4 | YES
21 | OK | 65 | 66 | 66 | 43 | 39.6 | 15.04 | 50 | 57.4 | 19.8 | 45.7 | 27 | 221.3 | 218.4 | 218.4 | YES
22 | OK | 70 | 3 | 30 | 6 | 41.6 | 21.78 | 50 | 57.4 | 19.8 | 41.4 | 29.9 | 220.3 | 222.6 | 220.3 | YES
| NG | 66 | 74 | 74 | 43 | 39.6 | 12.91 | 50 | 57.4 | 19.8 | 0 | 26 | 148.5 | 218.5 | 148.5 | NO
23 | OK | 3 | 2 | 27 | 49 | 52.5 | 18.97 | 50 | 57.4 | 19.8 | 43.4 | 27.3 | 220.3 | 222.7 | 220.3 | YES
| NG | 74 | 60 | 60 | 43 | 39.8 | 12.91 | 50 | 57.4 | 19.8 | 258.5 | 26 | 22.5 | 218.5 | 22.5 | NO
24 | OK | 2 | 31 | 31 | 6 | 60.9 | 12.65 | 50 | 57.4 | 19.8 | 48.1 | 24.3 | 220.1 | 223.1 | 220.1 | YES
25 | OK | 2 | 68 | 27 | 49 | 52.5 | 6.32 | 50 | 57.4 | 19.8 | 52.7 | 22.7 | 219.8 | 223 | 219.8 | YES
26 | OK | 60 | 61 | 61 | 43 | 42.4 | 12.91 | 50 | 57.4 | 19.8 | 47.8 | 26 | 221.1 | 218.6 | 218.6 | YES
27 | OK | 31 | 8 | 8 | 6 | 100.6 | 8.46 | 50 | 57.4 | 19.8 | 51.1 | 23.7 | 220 | 223.1 | 220 | YES
28 | OK | 68 | 28 | 27 | 49 | 52.5 | 5.94 | 50 | 57.4 | 19.8 | 53 | 22.5 | 219.8 | 223.1 | 219.8 | YES
29 | OK | 61 | 46 | 40 | 0 | 47.7 | 11.91 | 50 | 57.4 | 19.8 | 48.5 | 25.5 | 221.1 | 219.1 | 219.1 | YES
30 | OK | 8 | 7 | 7 | 6 | 140.4 | 7.56 | 50 | 57.4 | 19.8 | 51.8 | 23.2 | 220 | 223.1 | 220 | YES
31 | OK | 28 | 29 | 27 | 49 | 52.5 | 5.66 | 50 | 57.4 | 19.8 | 53.2 | 22.4 | 219.8 | 223.1 | 219.8 | YES
32 | OK | 46 | 38 | 40 | 0 | 47.7 | 11.91 | 50 | 57.4 | 19.8 | 48.5 | 25.5 | 221.1 | 219.1 | 219.1 | YES
33 | ** OPTIMAL ** | 29 | 27 | 27 | 49 | 52.5 | 4.28 | 50 | 57.4 | 19.8 | 0 | 21.7 | 223.2 | 223.1 | 223.1 | YES
34 | OK | 38 | 39 | 40 | 0 | 47.7 | 9.57 | 50 | 57.4 | 19.8 | 49.9 | 24.4 | 221 | 220.2 | 220.2 | YES
35 | OK | 27 | 51 | 51 | 49 | 52.5 | 1.58 | 50 | 57.4 | 19.8 | 56.1 | 20.5 | 219.7 | 223.2 | 219.7 | YES
36 | OK | 39 | 53 | 40 | 0 | 47.7 | 8.29 | 50 | 57.4 | 19.8 | 50.3 | 23.7 | 221 | 220.1 | 220.1 | YES
37 | OK | 51 | 34 | 34 | 49 | 52.7 | 1.58 | 50 | 57.4 | 19.8 | 56.2 | 20.5 | 219.7 | 223.2 | 219.7 | YES
38 | OK | 53 | 54 | 40 | 0 | 47.7 | 8.29 | 50 | 57.4 | 19.8 | 51.2 | 23.7 | 221 | 220.1 | 220.1 | YES
39 | OK | 34 | 32 | 32 | 49 | 54.4 | 0.57 | 50 | 57.4 | 19.8 | 57 | 20 | 219.7 | 223.2 | 219.7 | YES
40 | OK | 54 | 40 | 40 | 0 | 47.7 | 5.16 | 50 | 57.4 | 19.8 | 53.6 | 22.2 | 219.6 | 220.3 | 219.6 | YES
41 | OK | 40 | 41 | 41 | 0 | 59.2 | 5.16 | 50 | 57.4 | 19.8 | 53.6 | 22.2 | 219.6 | 220.6 | 219.6 | YES
42 | OK | 41 | 42 | 42 | 0 | 91.3 | 2.49 | 50 | 57.4 | 19.8 | 55.5 | 20.9 | 220 | 221.6 | 220 | YES
43 | OK | 42 | 47 | 47 | 0 | 102.4 | 1.84 | 50 | 57.4 | 19.8 | 56 | 20.6 | 219 | 221.7 | 219 | YES
44 | OK | 47 | 44 | 44 | 0 | 119.9 | 1.84 | 50 | 57.4 | 19.8 | 56 | 20.6 | 219 | 221.8 | 219 | YES

## Summary
Parameter | Value
TR_A (overloaded) | 60-013943
TR_B (available) | 66-025604
TR_A Rated kVA | 160
TR_B Rated kVA | 250
TR_A Baseline Loading% | 57.4
TR_B Baseline Loading% | 19.8
Total Scenarios Evaluated | 51
Feasible Scenarios | 44
--- Optimal Solution ---
Switch Parent Node | 29
Switch Child Node | 27
Tie Node (TR_A side) | 27
Tie Node (TR_B side) | 49
Tie Line Distance (m) | 52.5
Load Transferred (kW) | 4.28
TR_A Loading After (%) | 0
TR_B Loading After (%) | 21.7
Minimum Voltage (V) | 223.1